## 26 MAR-01APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 02 APR-08APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED

## 09 APR-15APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED

## 16APR-22APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16

## 23APR-29APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16

## 30APR-06MAY18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED

## 07MAY-13MAY18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED

## 14MAY-20MAY18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED

## 21MAY-27MAY18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED

## 28MAY-03JUN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED

## 04JUN-10JUN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED

## 11JUN-17JUN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED

## 18JUN-24JUN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED

## 25JUN-01JUL18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | MN-15 | Imphal(PG) end Of Loktak | NP-8672-A | Y | N | N | 2018-05-24 | OTHER END USED |  |  | Reading 40% lower than the other end.

## 02JUL-08JUL18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | NO | NO | YES | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | NO | NO | YES | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | YES | NO | NO | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | NO | YES | NO | 2018-04-16
5 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | NO | YES | NO | 2018-04-16
6 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | NO | YES | NO | 2018-04-16
7 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | NO | YES | NO | 2018-04-16
8 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | NO | YES | NO | 2018-04-16
9 | MANIPUR | IMPHAL(S) | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
11 | TRIPURA | 79 TILLA | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
13 | MANIPUR | NINGTHOUKHONG | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | NO | NO | YES | 2018-05-24 | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | Imphal(PG) end Of Loktak | NP-8672-A | YES | NO | NO | 2018-05-24 | OTHER END USED |  |  | Reading 40% lower than the other end.
[5 empty] | 2 | 9 | 3

## 09JUL-15JUL18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | MN-15 | Imphal(PG) end Of Loktak | NP-8672-A | Y | N | N | 2018-05-24 | OTHER END USED |  |  | Reading 40% lower than the other end.

## 16JUL-22JUL18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
14 | MANIPUR | NINGTHOUKHONG | MN-15 | Imphal(PG) end Of Loktak | NP-8672-A | Y | N | N | 2018-05-24 | OTHER END USED |  | 2018-07-22 | Reading 40% lower than the other end.

## 23JUL-29JUL18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | TRIPURA | 79 TILLA | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | MANIPUR | NINGTHOUKHONG | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
14 | ASSAM | SAMAGURI | SAMAGURI END OF MISA I | NP-5797-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
15 | ASSAM | SAMAGURI | SAMAGURI END OF MISA II | NP-5796-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
16 | ASSAM | MARIANI | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
[5 empty] | 1 | 12 | 3

## 30JUL-05AUG18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | NO | NO | YES | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | NO | NO | YES | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | YES | NO | NO | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | NO | YES | NO | 2018-04-16
5 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | NO | YES | NO | 2018-04-16
6 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | NO | YES | NO | 2018-04-16
7 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | NO | YES | NO | 2018-04-16
8 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | NO | YES | NO | 2018-04-16
9 | MANIPUR | IMPHAL(S) | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | NINGTHOUKHONG | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | NO | NO | YES | 2018-05-24 | OTHER END USED
12 | ASSAM | MARIANI | MARIANI END OF KATHALGURI | NP-6888-A | NO | YES | NO | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
13 | ASSAM | PANCHGRAM | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | YES | NO | NO | 2018-07-30 | OTHER END USED
[5 empty] | 2 | 8 | 3

## 06AUG-12AUG18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
12 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
13 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
[6 empty] | 2 | 8 | 3

## 13AUG-19AUG18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
12 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
13 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 20AUG-26AUG18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
5 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
9 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
12 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
13 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 27AUG-02SEPT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | NO | NO | yes | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | NO | NO | yes | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | yes | NO | NO | 2018-04-02 | OTHER END USED
4 | POWERGRID | BONGAIGAON | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | NO | yes | NO | 2018-04-16
5 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | NO | yes | NO | 2018-04-16
6 | POWERGRID | BONGAIGAON | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | NO | yes | NO | 2018-04-16
7 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | NO | yes | NO | 2018-04-16
8 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | NO | yes | NO | 2018-04-16
9 | MANIPUR | IMPHAL(S) | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | NO | yes | NO | 2018-04-30 |  |  |  | OTHER END USED
10 | MANIPUR | IMPHAL(S) | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | NO | yes | NO | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | NINGTHOUKHONG | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | NO | NO | yes | 2018-05-24 | OTHER END USED
12 | ASSAM | MARIANI | MARIANI END OF KATHALGURI | NP-6888-A | NO | yes | NO | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
13 | ASSAM | PANCHGRAM | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | yes | NO | NO | 2018-07-30 | OTHER END USED
14 | ASSAM | SILCHAR | Silchar end of 132 kV PK'BARI-1 | NP-8569-A | NO | NO | yes | 2018-08-27 | OTHER END USED
[5 empty] | 2 | 8 | 4

## 03SEP-09SEPT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | NO | NO | YES | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | NO | NO | YES | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | YES | NO | NO | 2018-04-02 | OTHER END USED
4 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | NO | YES | NO | 2018-04-16
5 | NTPC | NTPC | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | NO | YES | NO | 2018-04-16
6 | MANIPUR | IMPHAL(S) | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | IMPHAL(S) | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | NO | YES | NO | 2018-04-30 |  |  |  | OTHER END USED
8 | MANIPUR | NINGTHOUKHONG | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | NO | NO | YES | 2018-05-24 | OTHER END USED
9 | ASSAM | MARIANI | MARIANI END OF KATHALGURI | NP-6888-A | NO | YES | NO | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
10 | ASSAM | PANCHGRAM | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | YES | NO | NO | 2018-07-30 | OTHER END USED
[5 empty] | 2 | 5 | 3

## 10SEP-16SEPT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
5 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
6 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
8 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
9 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
10 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 17SEP-23SEPT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
5 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
6 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
8 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
9 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
10 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 24SEP-30SEPT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
5 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
6 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
8 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
9 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
10 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 01OCT-07OCT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
5 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
6 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
8 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
9 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
10 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 08OCT-14OCT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
2 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
3 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
4 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
5 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
6 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
8 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
9 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
10 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 15OCT-21OCT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
3 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
4 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
5 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
6 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
8 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
9 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 22OCT-28OCT18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
3 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
4 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
5 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
6 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
7 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
8 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
9 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 29OCT-04NOV18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED |  | 2018-10-29

## 05NOV-11NOV18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 12NOV-18NOV18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16 |  |  | 2018-11-12
8 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16 |  |  | 2018-11-12

## 19NOV-25NOV18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 26NOV18-02DEC18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 03DEC18-09DEC18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 10DEC18-16DEC18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 17DEC18-23DEC18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED

## 24DEC18-30DEC18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED | solved at 30.12.18 |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 31DEC18-06JAN19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(MAN) END OF JIRIBAM(PG) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED | solved |  | JIRIBAM(PG) END IS READING ZERO VALUE
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 07JAN-13JAN19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
8 | ASSAM | PAILAPOOL | AS-10 | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | N | N | Y | 2019-01-08 |  |  |  | PAILAPOOL END IS READING 16% LESS

## 14JAN-20JAN19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
8 | ASSAM | PAILAPOOL | AS-10 | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | N | N | Y | 2019-01-08 |  |  |  | PAILAPOOL END IS READING 16% LESS

## 21 JAN-27JAN 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
8 | ASSAM | PAILAPOOL | AS-10 | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | N | N | Y | 2019-01-08 |  |  |  | PAILAPOOL END IS READING 16% LESS

## 28 JAN-03 FEB19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
8 | ASSAM | PAILAPOOL | AS-10 | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | N | N | Y | 2019-01-08 |  |  |  | PAILAPOOL END IS READING 16% LESS

## 04 Feb19-10 Feb 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
8 | ASSAM | PAILAPOOL | AS-10 | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | N | N | Y | 2019-01-08 |  |  |  | PAILAPOOL END IS READING 16% LESS

## 11 Feb -17 Feb 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | ASSAM | PANCHGRAM | AS-07 | PANCHGRAM END OF BDP(PG)FDR | NP-6872-A | Y | N | N | 2018-07-30 | OTHER END USED
7 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
8 | ASSAM | PAILAPOOL | AS-10 | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | N | N | Y | 2019-01-08 |  |  |  | PAILAPOOL END IS READING 16% LESS

## 18feb-24feb 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
7 | ASSAM | PAILAPOOL | AS-10 | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | N | N | Y | 2019-01-08 |  |  |  | PAILAPOOL END IS READING 16% LESS
8 | TRIPURA | DHARMANAGAR | TR-06 | D'NGAR END OF DULLAVCHERRA FDR | NP-6892-B | N | N | Y | 2019-02-18 | OTHER END USED

## 25 feb-03 mar
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED
7 | TRIPURA | DHARMANAGAR | TR-06 | D'NGAR END OF DULLAVCHERRA FDR | NP-6892-B | N | N | Y | 2019-02-18 | OTHER END USED |  |  | RESOLVED ON 4-03-19

## 04 MAR-10 MAR 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 11 MAR-17 MAR
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
3 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
4 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
5 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
6 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 18mar-24mar
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
3 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 25MAR-31MAR
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
3 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 01 APR-07 APR19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
3 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 08 APR-14 APR 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
3 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9675-A | Y | N | N | 2018-12-27 | OTHER END USED

## 15 APR-21 APR 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
3 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED

## 22 APR-28 APR 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
3 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED

## 29 APR-05 MAY 19
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | JIRIBAM | MN-19 | JIRIBAM(man) END OF JIRIBAM(pg) FDR | NP-8645-A | Y | N | N | 2018-12-31 | OTHER END USED |  |  | JIRIBAM(MAN) END IS READING 1/3 OF OTHER END
2 | MANIPUR | NINGTHOUKHONG | MN-17 | NINGTHOUKHONG end Of Imphal(PG) | NP-9521-A | N | N | Y | 2018-05-24 | OTHER END USED
3 | ASSAM | MARIANI | AS-03 | MARIANI END OF KATHALGURI | NP-6888-A | N | Y | N | 2018-07-23 | OTHER END USED |  |  | VERY HIGH TIME DRIFT;OTHER END USED