## 28 MAR -03 APR 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-04-07 | Year: | 2021-2022
| Period: | 2022-03-28 | To: | 2022-04-03
|  | Total number of Interface Meters | 546
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
2 | NAGALAND | MOKUKCHUNG | NG-05 | 132KV MOKOKCHUNG END OF DOYANG FDR | NP-9671-A | Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
3 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-02-14 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
4 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
5 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
6 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-01-10 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
4 | ASSAM | KAHILIPARA | AS-01 | 132 kV KAHILIPRA END OF UMTRU-1 | NP-8490 A | High time drift | 2022-02-07 | Till end of the week | KAHILIPARA | Other end meter used for drawal computation; Meter replacement required
5 | ASSAM | KAHILIPARA | AS-02 | 132 kV KAHILIPRA END OF UMTRU-2 | NP-8488 A | High time drift | 2022-02-07 | Till end of the week | KAHILIPARA | Other end meter used for drawal computation;Meter replacement required
6 | MIZORAM | KOLASIB | MZ-11 | 132 kV KOLASIB END OF BADARPUR(PG) FDR | NP-8497-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation; Meter replacement required
7 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NP-8496-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation;Meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - IMPHAL -2 | NP-9971-A | Line Meter | Weekly Drift correction required
5 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
9 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
10 | OTPC | PALATANA |  | GTG1 | NE-0033-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
24 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 400 kV MISA-BALIPARA 2 | NP-5291 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
29 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
30 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
31 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTCCPP GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTCCPP STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 04 APR -10 APR 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-04-13 | Year: | 2022-2023
| Period: | 2022-04-04 | To: | 2022-04-10
|  | Total number of Interface Meters | 546
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
2 | NAGALAND | MOKUKCHUNG | NG-05 | 132KV MOKOKCHUNG END OF DOYANG FDR | NP-9671-A | Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
3 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
4 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | ASSAM | KAHILIPARA | AS-01 | 132 kV KAHILIPRA END OF UMTRU-1 | NP-8490 A | High time drift | 2022-02-07 | Till end of the week | KAHILIPARA | Other end meter used for drawal computation; Meter replacement required
3 | ASSAM | KAHILIPARA | AS-02 | 132 kV KAHILIPRA END OF UMTRU-2 | NP-8488 A | High time drift | 2022-02-07 | Till end of the week | KAHILIPARA | Other end meter used for drawal computation;Meter replacement required
4 | MIZORAM | KOLASIB | MZ-11 | 132 kV KOLASIB END OF BADARPUR(PG) FDR | NP-8497-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation; Meter replacement required
5 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NP-8496-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation;Meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - IMPHAL -2 | NP-9971-A | Line Meter | Weekly Drift correction required
5 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
9 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
10 | OTPC | PALATANA |  | GTG1 | NE-0033-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
24 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 400 kV MISA-BALIPARA 2 | NP-5291 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
29 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
30 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
31 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTCCPP GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTCCPP STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 11 APR -17 APR 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-04-21 | Year: | 2022-2023
| Period: | 2022-04-11 | To: | 2022-04-17
|  | Total number of Interface Meters | 546
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
2 | NAGALAND | MOKUKCHUNG | NG-05 | 132KV MOKOKCHUNG END OF DOYANG FDR | NP-9671-A | Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
3 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
4 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | ASSAM | KAHILIPARA | AS-01 | 132 kV KAHILIPRA END OF UMTRU-1 | NP-8490 A | High time drift | 2022-02-07 | Till end of the week | KAHILIPARA | Other end meter used for drawal computation; Meter replacement required
3 | ASSAM | KAHILIPARA | AS-02 | 132 kV KAHILIPRA END OF UMTRU-2 | NP-8488 A | High time drift | 2022-02-07 | Till end of the week | KAHILIPARA | Other end meter used for drawal computation;Meter replacement required
4 | MIZORAM | KOLASIB | MZ-11 | 132 kV KOLASIB END OF BADARPUR(PG) FDR | NP-8497-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation; Meter replacement required
5 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NP-8496-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation;Meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - IMPHAL -2 | NP-9971-A | Line Meter | Weekly Drift correction required
5 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
9 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
10 | OTPC | PALATANA |  | GTG1 | NE-0033-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
24 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 400 kV MISA-BALIPARA 2 | NP-5291 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
29 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
30 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
31 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTCCPP GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTCCPP STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 18 APR -24 APR 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-04-28 | Year: | 2022-2023
| Period: | 2022-04-18 | To: | 2022-04-24
|  | Total number of Interface Meters | 546
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
2 | NAGALAND | MOKUKCHUNG | NG-05 | 132KV MOKOKCHUNG END OF DOYANG FDR | NP-9671-A | Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
3 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
4 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
6 | POWERGRID | MISA | AS-35 | 400 kV MISA END OF BALIPARA-1 FDR | NP-5299-A | Reads 40 % less | 2022-04-18 | Till end of the week | MISA | CT/PT connectivity checking required
7 | POWERGRID | BALIPARA | ZZ-07 | 400 kV BALIPARA END OF MISA-2 FDR | NP-5285-A | Reads 15 % less | 2022-04-18 | Till end of the week | BALIPARA | CT/PT connectivity checking required
8 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
9 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | ASSAM | KAHILIPARA | AS-01 | 132 kV KAHILIPRA END OF UMTRU-1 | NP-8490 A | High time drift | 2022-02-07 | 2022-04-19 | KAHILIPARA | New meter installed
3 | ASSAM | KAHILIPARA | AS-02 | 132 kV KAHILIPRA END OF UMTRU-2 | NP-8488 A | High time drift | 2022-02-07 | 2022-04-19 | KAHILIPARA | New meter installed
4 | MIZORAM | KOLASIB | MZ-11 | 132 kV KOLASIB END OF BADARPUR(PG) FDR | NP-8497-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation; Meter replacement required
5 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NP-8496-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation;Meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - IMPHAL -2 | NP-9971-A | Line Meter | Weekly Drift correction required
5 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
9 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
10 | OTPC | PALATANA |  | GTG1 | NE-0033-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
24 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 400 kV MISA-BALIPARA 2 | NP-5291 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
29 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
30 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
31 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTCCPP GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTCCPP STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 25 APR -01 MAY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-05-05 | Year: | 2022-2023
| Period: | 2022-04-25 | To: | 2022-05-01
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
2 | NAGALAND | MOKUKCHUNG | NG-05 | 132KV MOKOKCHUNG END OF DOYANG FDR | NP-9671-A | Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
3 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
4 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
6 | POWERGRID | MISA | AS-35 | 400 kV MISA END OF BALIPARA-1 FDR | NP-5299-A | Reads 40 % less | 2022-04-18 | Till end of the week | MISA | CT/PT connectivity checking required
7 | POWERGRID | BALIPARA | ZZ-07 | 400 kV BALIPARA END OF MISA-2 FDR | NP-5285-A | Reads 15 % less | 2022-04-18 | Till end of the week | BALIPARA | CT/PT connectivity checking required
8 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
9 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | MIZORAM | KOLASIB | MZ-11 | 132 kV KOLASIB END OF BADARPUR(PG) FDR | NP-8497-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation; Meter replacement required
3 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NP-8496-A | High time drift | 2022-02-21 | Till end of the week | KOLASIB | Other end meter used for drawal computation;Meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - IMPHAL -2 | NP-9971-A | Line Meter | Weekly Drift correction required
5 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
9 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
10 | OTPC | PALATANA |  | GTG1 | NE-0033-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
24 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
29 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
30 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AGTCCPP |  | AGTCCPP GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTCCPP STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 02 MAY-08 MAY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-05-12 | Year: | 2022-2023
| Period: | 2022-05-02 | To: | 2022-05-08
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
2 | NAGALAND | MOKUKCHUNG | NG-05 | 132KV MOKOKCHUNG END OF DOYANG FDR | NP-9671-A | Sign reversal | 2022-01-31 | 2022-05-08 | NAGALAND | CT connectivity checked and rectified
3 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
4 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
6 | POWERGRID | MISA | AS-35 | 400 kV MISA END OF BALIPARA-1 FDR | NP-5299-A | Reads 40 % less | 2022-04-18 | 2022-05-06 | MISA | CT/PT connectivity checked and rectified
7 | POWERGRID | BALIPARA | ZZ-07 | 400 kV BALIPARA END OF MISA-2 FDR | NP-5285-A | Reads 15 % less | 2022-04-18 | 2022-05-05 | BALIPARA | CT/PT connectivity checked and rectified
8 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
9 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | MIZORAM | KOLASIB | MZ-11 | 132 kV KOLASIB END OF BADARPUR(PG) FDR | NP-8497-A | High time drift | 2022-02-21 | 2022-05-08 | KOLASIB | New meter installed
3 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NP-8496-A | High time drift | 2022-02-21 | 2022-05-08 | KOLASIB | New meter installed
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 09 MAY-15 MAY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-05-19 | Year: | 2022-2023
| Period: | 2022-05-09 | To: | 2022-05-15
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | Till end of the week | NAGALAND | Other end meter used for drawal computation; CT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 16 MAY-22 MAY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-05-26 | Year: | 2022-2023
| Period: | 2022-05-16 | To: | 2022-05-22
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | DIMAPUR | NG-11 | 132KV DIMAPUR(S) END OF 132KV DIMAPUR(PG) I FDR | NP-5777-A | Erroneous reading, Sign reversal | 2022-01-31 | 2022-05-20 | NAGALAND | CT connectivity checked and rectified
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 400kV PALATANA - SILCHAR 2 | NE-0010-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
8 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 23 MAY-29 MAY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-06-02 | Year: | 2022-2023
| Period: | 2022-05-23 | To: | 2022-05-29
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 30 MAY-05 JUNE 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-06-09 | Year: | 2022-2023
| Period: | 2022-05-30 | To: | 2022-06-05
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | JIRIBAM | MN-19 | 132 kV JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Sign reversal | 2022-03-22 | 2022-05-30 | MANIPUR | CT connectivity checked and rectified
4 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 06 JUNE-12 JUNE 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-06-16 | Year: | 2022-2023
| Period: | 2022-06-06 | To: | 2022-06-12
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | Till end of the week | TRIPURA | Other end meter used for drawal computation; connectivity checking required
2 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 13 JUNE-19 JUNE 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-06-23 | Year: | 2022-2023
| Period: | 2022-06-13 | To: | 2022-06-19
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Erratic reading | 2021-07-26 | 2022-06-16 | TRIPURA | New meter installed
2 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | 400 KV NEW KOHIMA - MARIANI-2 | NP-9973-A | Line Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
7 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | BALIPARA |  | 220/132 kV BALIPARA ICT-1 (LV) | NP-6891-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BALIPARA |  | 400 kV BALIPARA-MISA -2 | NP-5285-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
27 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 20 JUNE-26 JUNE 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-06-30 | Year: | 2022-2023
| Period: | 2022-06-20 | To: | 2022-06-26
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 27 JUNE-03 JULY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-07-07 | Year: | 2022-2023
| Period: | 2022-06-27 | To: | 2022-07-03
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 04 JULY-10 JULY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-07-14 | Year: | 2022-2023
| Period: | 2022-07-04 | To: | 2022-07-10
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 11 JULY-17 JULY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-07-21 | Year: | 2022-2023
| Period: | 2022-07-11 | To: | 2022-07-17
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
4 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
5 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
6 | OTPC | PALATANA |  | STG1 | NP-7600-A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | AGTPP GTG-1 | NP-9479-A | Standby Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | AGTPP GTG-2 | NP-9605-A | Standby Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | AGTPP GTG-4 | NP-9517-A | Standby Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | AGTPP STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9513-A | Check Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9514-A | Check Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9080-A | Main Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9515-A | Check Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9940-A | Main Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9941-A | Main Meter | Weekly Drift correction required
| NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required
| MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required

## 18 JULY-24 JULY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-07-28 | Year: | 2022-2023
| Period: | 2022-07-18 | To: | 2022-07-24
|  | Total number of Interface Meters | 548
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AGTCCPP |  | AGTPP GTG-1 | NP-9479-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTPP GTG-2 | NP-9605-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTPP GTG-4 | NP-9517-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | AGTPP STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9513-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9514-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9080-A | Main Meter | Weekly Drift correction required
40 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9515-A | Check Meter | Weekly Drift correction required
41 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9940-A | Main Meter | Weekly Drift correction required
42 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
43 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9941-A | Main Meter | Weekly Drift correction required
44 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 25 JULY-31 JULY 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-08-04 | Year: | 2022-2023
| Period: | 2022-07-25 | To: | 2022-07-31
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
7 | TRIPURA | DHARMANAGAR | TR-06 | 132KV DHARMANAGAR END OF DULLAVCHERA | NP-6892-B | Erroneous reading | 2022-07-28 | Till end of the week | DULLAVCHERA | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO-RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AGTCCPP |  | AGTPP GTG-1 | NP-9479-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTPP GTG-2 | NP-9605-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTPP GTG-4 | NP-9517-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | AGTPP STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9513-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9514-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9080-A | Main Meter | Weekly Drift correction required
40 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9515-A | Check Meter | Weekly Drift correction required
41 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9940-A | Main Meter | Weekly Drift correction required
42 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
43 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9941-A | Main Meter | Weekly Drift correction required
44 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 01 AUG-07 AUG 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-08-11 | Year: | 2022-2023
| Period: | 2022-08-01 | To: | 2022-08-07
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
7 | TRIPURA | DHARMANAGAR | TR-06 | 132KV DHARMANAGAR END OF DULLAVCHERA | NP-6892-B | Erroneous reading | 2022-07-28 | Till end of the week | DULLAVCHERA | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AGTCCPP |  | AGTPP GTG-1 | NP-9479-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTPP GTG-2 | NP-9605-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTPP GTG-4 | NP-9517-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | AGTPP STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9513-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9514-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9080-A | Main Meter | Weekly Drift correction required
40 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9515-A | Check Meter | Weekly Drift correction required
41 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9940-A | Main Meter | Weekly Drift correction required
42 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
43 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9941-A | Main Meter | Weekly Drift correction required
44 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 08 AUG-14 AUG 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-08-18 | Year: | 2022-2023
| Period: | 2022-08-08 | To: | 2022-08-14
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
7 | TRIPURA | DHARMANAGAR | TR-06 | 132KV DHARMANAGAR END OF DULLAVCHERA | NP-6892-B | Erroneous reading | 2022-07-28 | 2022-08-14 | DULLAVCHERA | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AGTCCPP |  | AGTPP GTG-1 | NP-9479-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTPP GTG-2 | NP-9605-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTPP GTG-4 | NP-9517-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | AGTPP STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9513-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9514-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9080-A | Main Meter | Weekly Drift correction required
40 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9515-A | Check Meter | Weekly Drift correction required
41 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9940-A | Main Meter | Weekly Drift correction required
42 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
43 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9941-A | Main Meter | Weekly Drift correction required
44 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 15 AUG-21 AUG 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-08-25 | Year: | 2022-2023
| Period: | 2022-08-15 | To: | 2022-08-21
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AGTCCPP |  | AGTPP GTG-1 | NP-9479-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AGTCCPP |  | AGTPP GTG-2 | NP-9605-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AGTCCPP |  | AGTPP GTG-4 | NP-9517-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AGTCCPP |  | AGTPP STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-1 FDR | NP-9513-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9093-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF AGARTALA-2 FDR | NP-9514-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9080-A | Main Meter | Weekly Drift correction required
40 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF K'GHAT FDR | NP-9515-A | Check Meter | Weekly Drift correction required
41 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9940-A | Main Meter | Weekly Drift correction required
42 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
43 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9941-A | Main Meter | Weekly Drift correction required
44 | NEEPCO | AGTCCPP |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 22 AUG-28 AUG 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-09-01 | Year: | 2022-2023
| Period: | 2022-08-22 | To: | 2022-08-28
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 33 % less | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 29 AUG-04 SEPT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-09-08 | Year: | 2022-2023
| Period: | 2022-08-29 | To: | 2022-09-04
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132KV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 05 SEPT-11 SEPT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-09-15 | Year: | 2022-2023
| Period: | 2022-09-05 | To: | 2022-09-11
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
7 | POWERGRID | SILCHAR | AS-75 | 132 kV SILCHAR END OF SRIKONA-I FDR | NP-9895-A | Erroneous reading | 2022-09-05 | Till end of the week | silchar | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 12 SEPT-18 SEPT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-09-22 | Year: | 2022-2023
| Period: | 2022-09-12 | To: | 2022-09-18
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
7 | POWERGRID | SILCHAR | AS-75 | 132 kV SILCHAR END OF SRIKONA-I FDR | NP-9895-A | Erroneous reading | 2022-09-05 | 2022-09-12 | silchar | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 19 SEPT-25 SEPT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-09-29 | Year: | 2022-2023
| Period: | 2022-09-19 | To: | 2022-09-25
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 26 SEPT-02 OCT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-10-06 | Year: | 2022-2023
| Period: | 2022-09-26 | To: | 2022-10-02
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 03 OCT-09 OCT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-10-13 | Year: | 2022-2023
| Period: | 2022-10-03 | To: | 2022-10-09
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | Till end of the week | ZIRO | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 10 OCT-16 OCT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-10-20 | Year: | 2022-2023
| Period: | 2022-10-10 | To: | 2022-10-16
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | Till end of the week | MANIPUR | Other end meter used for drawal computation; CT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | ZIRO | AR-06 | 132kV ZIRO END OF RANGANADI | NP-9704-A | High time drift | 2022-05-30 | 2022-10-16 | ZIRO | Time drift correction done
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 17 OCT-23 OCT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-10-27 | Year: | 2022-2023
| Period: | 2022-10-17 | To: | 2022-10-23
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | Till end of the week | DEOMALI | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | MANIPUR | RENGPANG | MN-11 | 132 kV RENGPANG END OF LOKTAK FEEDER | NP-9512-A | Sign reversal | 2022-03-21 | 2022-10-18 | MANIPUR | CT connectivity checked and rectified
4 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
6 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
| ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG)-2 | NP-9603-A | Standby Meter | Weekly Drift correction required
6 | MIZORAM | KOLASIB |  | 132 kV KOLASIB END OF AIZAWL(PG) | NE-0087-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF 400 PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
25 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
26 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
27 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
28 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR I FDR | NP-9558-A | Check Meter | Weekly Drift correction required
29 | OTPC | PALATANA |  | 400 kV PALATANA END OF SLCHAR II FDR | NP-9560-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132 kV PALATANA END OF UDAIPUR FDR | NP-9559-A | Standby Meter | Weekly Drift correction required

## 24 OCT-30 OCT 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-11-03 | Year: | 2022-2023
| Period: | 2022-10-24 | To: | 2022-10-30
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | AR-07 | 220KV DEOMALI END OF KATHALGURI FDR | NP-9659-A | Reads 2/3 of other end | 2022-05-23 | 2022-10-27 | DEOMALI | CT connectivity checked and rectified
2 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
5 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
31 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
32 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
33 | OTPC | PALATANA |  | 400 kV PALATANA END OF SM NAGAR (STERLITE)-1 | NP-9944-A | Main Meter | Weekly Drift correction required
34 | OTPC | PALATANA |  | 132 kV PALATANA END OF SM NAGAR FDR | NP-9561-A | Main Meter | Weekly Drift correction required

## 31 OCT-06 NOV 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-11-10 | Year: | 2022-2023
| Period: | 2022-10-31 | To: | 2022-11-06
|  | Total number of Interface Meters | 532
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
31 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
32 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
33 | OTPC | PALATANA |  | 400 kV PALATANA END OF SM NAGAR (STERLITE)-1 | NP-9944-A | Main Meter | Weekly Drift correction required
34 | OTPC | PALATANA |  | 132 kV PALATANA END OF SM NAGAR FDR | NP-9561-A | Main Meter | Weekly Drift correction required

## 07 NOV-13 NOV 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-11-17 | Year: | 2022-2023
| Period: | 2022-11-07 | To: | 2022-11-13
|  | Total number of Interface Meters | 535
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
31 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
32 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
33 | OTPC | PALATANA |  | 400 kV PALATANA END OF SM NAGAR (STERLITE)-1 | NP-9944-A | Main Meter | Weekly Drift correction required
34 | OTPC | PALATANA |  | 132 kV PALATANA END OF SM NAGAR FDR | NP-9561-A | Main Meter | Weekly Drift correction required

## 14 NOV-20 NOV 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-11-24 | Year: | 2022-2023
| Period: | 2022-11-14 | To: | 2022-11-20
|  | Total number of Interface Meters | 537
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
31 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
32 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
33 | OTPC | PALATANA |  | 400 kV PALATANA END OF SM NAGAR (STERLITE)-1 | NP-9944-A | Main Meter | Weekly Drift correction required
34 | OTPC | PALATANA |  | 132 kV PALATANA END OF SM NAGAR FDR | NP-9561-A | Main Meter | Weekly Drift correction required

## 21 NOV-27 NOV 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-12-01 | Year: | 2022-2023
| Period: | 2022-11-21 | To: | 2022-11-27
|  | Total number of Interface Meters | 537
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
31 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
32 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
33 | OTPC | PALATANA |  | 400 kV PALATANA END OF SM NAGAR (STERLITE)-1 | NP-9944-A | Main Meter | Weekly Drift correction required
34 | OTPC | PALATANA |  | 132 kV PALATANA END OF SM NAGAR FDR | NP-9561-A | Main Meter | Weekly Drift correction required

## 28 NOV-04 DEC 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-12-08 | Year: | 2022-2023
| Period: | 2022-11-28 | To: | 2022-12-04
|  | Total number of Interface Meters | 537
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | 132kV PALATANA - SM NAGAR | NP-8381-A | Check Meter | Weekly Drift correction required
31 | OTPC | PALATANA |  | 132kV PALATANA - UDAIPUR | NP-9470-A | Check Meter | Weekly Drift correction required
32 | OTPC | PALATANA |  | PALATANA STG I | NP-7600-A | Standby Meter | Weekly Drift correction required
33 | OTPC | PALATANA |  | 400 kV PALATANA END OF SM NAGAR (STERLITE)-1 | NP-9944-A | Main Meter | Weekly Drift correction required
34 | OTPC | PALATANA |  | 132 kV PALATANA END OF SM NAGAR FDR | NP-9561-A | Main Meter | Weekly Drift correction required

## 05 DEC-11 DEC 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-12-15 | Year: | 2022-2023
| Period: | 2022-12-05 | To: | 2022-12-11
|  | Total number of Interface Meters | 537
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 12 DEC-18 DEC 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-12-21 | Year: | 2022-2023
| Period: | 2022-12-12 | To: | 2022-12-18
|  | Total number of Interface Meters | 539
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 19 DEC-25 DEC 2022
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2022-12-29 | Year: | 2022-2023
| Period: | 2022-12-19 | To: | 2022-12-25
|  | Total number of Interface Meters | 539
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 26 DEC-01 JAN 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-01-05 | Year: | 2022-2023
| Period: | 2022-12-26 | To: | 2023-01-01
|  | Total number of Interface Meters | 539
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 02 JAN-08 JAN 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-01-12 | Year: | 2022-2023
| Period: | 2023-01-02 | To: | 2023-01-08
|  | Total number of Interface Meters | 539
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 09 JAN-15 JAN 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-01-19 | Year: | 2022-2023
| Period: | 2023-01-09 | To: | 2023-01-15
|  | Total number of Interface Meters | 539
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 16 JAN-22 JAN 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-01-25 | Year: | 2022-2023
| Period: | 2023-01-16 | To: | 2023-01-22
|  | Total number of Interface Meters | 539
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL END OF IMPHAL(PG)-2 FDR | NP-9603-A | High Time drift | 2022-04-04 | Till end of the week | THOUBAL | Time drift corrective action required
2 | MIZORAM | KOLASIB | MZ-12 | 132 kV KOLASIB END OF AIZAWL(PG) FDR | NE-0087-A | High Time drift | 2022-07-18 | Till end of the week | KOLASIB | Time drift corrective action required
3 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
4 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 23 JAN-29 JAN 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-02-02 | Year: | 2022-2023
| Period: | 2023-01-23 | To: | 2023-01-29
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2022-11-14 | 2023-01-23 | DHARMANAGAR | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 30 JAN-05 FEB 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-02-09 | Year: | 2022-2023
| Period: | 2023-01-30 | To: | 2023-02-05
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-1 HV Side | NE-0050-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | SILCHAR |  | 400 kV SILCHAR- BYRNIHAT- 2 | NP-9398-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | SILCHAR |  | 400/132kV SILCHAR 200MVA ICT-2 HV Side | NE-0049-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-II | NE-0042-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PALATANA-I | NE-0030-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-1 | NP-9925-A | Line Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | 400/132 SILCHAR-MISA FEEDER-II | NP-9896-A | Line Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-2 | NE-0040-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF PK BARI (STERLITE)-1 | NP-9901-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | 400 kV SILCHAR END OF IMPHAL-1 | NE-0007-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-1 | NE-0007-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SILCHAR |  | 132 kV SILCHAR END OF SRIKONA-2 | NP-9897-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 06 FEB-12 FEB 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-02-16 | Year: | 2022-2023
| Period: | 2023-02-06 | To: | 2023-02-12
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | MIRZA END OF 400 KV SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | KARIMGANJ | AM-54 | 132 kV KARIMGANJ END OF KUMARGHAT | NP-9937-A | Erroneous reading | 2023-02-06 | Till end of the week | KARIMGANJ | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 13 FEB-19 FEB 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-02-23 | Year: | 2022-2023
| Period: | 2023-02-13 | To: | 2023-02-19
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | MIRZA END OF 400 KV SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | KARIMGANJ | AM-54 | 132 kV KARIMGANJ END OF KUMARGHAT | NP-9937-A | Erroneous reading | 2023-02-06 | Till end of the week | KARIMGANJ | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | POWERGRID | NEW MARIANI | AS-94 | 220kV NEW MARIANI END OF AGBPP | NE-0034-A | Reads 50 % less | 2023-02-17 | Till end of the week | NEW MARIANI | Other end meter used for Injection calculation/ CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 20 FEB-26 FEB 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-03-02 | Year: | 2022-2023
| Period: | 2023-02-20 | To: | 2023-02-26
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads 50 % less | 2022-04-18 | 2023-02-26 | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads 50 % less | 2022-04-18 | 2023-02-26 | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | Till end of the week | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | MIRZA END OF 400 KV SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | KARIMGANJ | AM-54 | 132 kV KARIMGANJ END OF KUMARGHAT | NP-9937-A | Erroneous reading | 2023-02-06 | Till end of the week | KARIMGANJ | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | POWERGRID | NEW MARIANI | AS-94 | 220kV NEW MARIANI END OF AGBPP | NE-0034-A | Reads 50 % less | 2023-02-17 | Till end of the week | NEW MARIANI | Other end meter used for Injection calculation/ CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 27 FEB-05 MAR 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-03-09 | Year: | 2022-2023
| Period: | 2023-02-27 | To: | 2023-03-05
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | MANIPUR | TIPAIMUKH | MN-20 | 132 kV TIPAIMUKH END OF AIZAWL FDR | NE-0169-A | Erroneous reading, Sign reversal | 2022-06-20 | 2023-03-05 | TIPAIMUKH | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | MIRZA END OF 400 KV SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | POWERGRID | NEW MARIANI | AS-94 | 220kV NEW MARIANI END OF AGBPP | NE-0034-A | Reads 50 % less | 2023-02-17 | Till end of the week | NEW MARIANI | Other end meter used for Injection calculation/ CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 06 MAR-12 MAR 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-03-16 | Year: | 2022-2023
| Period: | 2023-03-06 | To: | 2023-03-12
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | ASSAM | MIRZA | AS-93 | MIRZA END OF 400 KV SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | POWERGRID | NEW MARIANI | AS-94 | 220kV NEW MARIANI END OF AGBPP | NE-0034-A | Reads 50 % less | 2023-02-17 | Till end of the week | NEW MARIANI | Other end meter used for Injection calculation/ CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | RANGIA |  | 132 kV RANGIA-MOTANGA | NP-9669 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 13 MAR-19 MAR 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-03-23 | Year: | 2022-2023
| Period: | 2023-03-13 | To: | 2023-03-19
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | ASSAM | MIRZA | AS-93 | MIRZA END OF 400 KV SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | POWERGRID | NEW MARIANI | AS-94 | 220kV NEW MARIANI END OF AGBPP | NE-0034-A | Reads 50 % less | 2023-02-17 | Till end of the week | NEW MARIANI | Other end meter used for Injection calculation/ CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 20 MAR-26 MAR 2023
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-03-30 | Year: | 2022-2023
| Period: | 2023-03-20 | To: | 2023-03-26
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | ASSAM | MIRZA | AS-93 | MIRZA END OF 400 KV SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | POWERGRID | NEW MARIANI | AS-94 | 220kV NEW MARIANI END OF AGBPP | NE-0034-A | Reads 50 % less | 2023-02-17 | 2023-03-24 | NEW MARIANI | Other end meter used for Injection calculation/ CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required

## 27 MAR-02 APR 2023 (hidden)
Interconnection Metering Error for North-Eastern Region
Date of Reporting |  | 2023-04-06 | Year: | 2022-2023
| Period: | 2023-03-27 | To: | 2023-04-02
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | sign reversal | 2023-02-27 | Till end of the week | DIMAPUR | CT/PT connectivity checking required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR | NP-9981-A | Erroneous reading | 2023-02-06 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading | 2023-03-27 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 KV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
9 | POWERGRID | SILCHAR |  | SILCHAR END 400/132 KV ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | LV SIDE OF 400/220KV BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | BONG END OF 220KV SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | BONGAIGAON END OF 400 KV NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required