## 03 APR-09 APR 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-04-12 | Year: | 2023-2024
| Period: | 2023-04-03 | To: | 2023-04-09
|  | Total number of Interface Meters | 543
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-04-03 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | MIRZA | AM-01 | 400 KV MIRZA END OF BONGAIGAON FDR | NP-9983-A | Erroneous reading,sign reversal | 2023-04-03 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-04-03 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
9 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
11 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
13 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 kV SILCHAR END ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400 kV BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 400 kV BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 400/220 kV LV SIDE OF BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 220 kV BONG END OF SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
25 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
31 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
32 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
33 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
34 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
35 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
36 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
37 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
38 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 10 APR-16 APR 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-04-20 | Year: | 2023-2024
| Period: | 2023-04-10 | To: | 2023-04-16
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-04-03 | 2023-04-09 | MIRZA | CT/PT connectivity checked and rectified.
7 | ASSAM | MIRZA | AM-01 | 400 KV MIRZA END OF BONGAIGAON FDR | NP-9983-A | Erroneous reading,sign reversal | 2023-04-03 | 2023-04-09 | MIRZA | CT/PT connectivity checked and rectified.
8 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-04-03 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
9 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
11 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
13 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | SILCHAR |  | 400/132 kV SILCHAR END ICT-3 (HV SIDE) | NP-6946-A | Line Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400 kV BONG END OF BINAGURI-1 FEEDER | NP-8468 A | Main Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 400 kV BONG END OF BINAGURI-2 FEEDER | NP-8469 A | Main Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 400/220 kV LV SIDE OF BONG ICT-2 | NP-5773 A | Line Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 220 kV BONG END OF SKL-2 FDR | NP-5780 A | Line Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR 2 | NP-9069 A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
25 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
31 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
32 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
33 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
34 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
35 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
36 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
37 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
38 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 17 APR-23 APR 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-04-27 | Year: | 2023-2024
| Period: | 2023-04-17 | To: | 2023-04-23
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-04-03 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
9 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
11 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
13 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
31 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 24 APR-30 APR 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-05-04 | Year: | 2023-2024
| Period: | 2023-04-24 | To: | 2023-04-30
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-04-03 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
9 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
11 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
13 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
31 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 01 MAY-07 MAY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-05-11 | Year: | 2023-2024
| Period: | 2023-05-01 | To: | 2023-05-07
|  | Total number of Interface Meters | 559
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-04-03 | 2023-05-07 | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | Till end of the week | TINSUKIA | Time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF HAFLONG | NE-0019-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
9 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
11 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
13 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
31 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 08 MAY-14 MAY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-05-18 | Year: | 2023-2024
| Period: | 2023-05-08 | To: | 2023-05-14
|  | Total number of Interface Meters | 559
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | 2023-05-15 | Till end of the week | Time drift error rectiifed
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | 2023-05-15 | Till end of the week | Time drift error rectiifed
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
10 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 15 MAY-21 MAY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-05-25 | Year: | 2023-2024
| Period: | 2023-05-15 | To: | 2023-05-21
|  | Total number of Interface Meters | 559
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | ASSAM | TINSUKIA | AS-53 | 220 kV TINSUKIA END OF KTG FDR-I | NP-9654-A | High Time drift | 2022-10-24 | 2023-05-15 | TINSUKIA | Time drift error rectiifed
2 | ASSAM | TINSUKIA | AS-74 | 220 kV TINSUKIA END OF KATHALGURI-II | NP-9658-A | High Time drift | 2022-10-24 | 2023-05-15 | TINSUKIA | Time drift error rectiifed
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
10 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 22 MAY-28 MAY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-06-01 | Year: | 2023-2024
| Period: | 2023-05-22 | To: | 2023-05-28
|  | Total number of Interface Meters | 559
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | DULLAVCHERA |  | 132 kV DULLAVCHERA- DHARMANAGAR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
10 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 29 MAY-04 JUNE 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-06-08 | Year: | 2023-2024
| Period: | 2023-05-29 | To: | 2023-06-04
|  | Total number of Interface Meters | 516
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
9 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
10 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 05 JUNE 23-11 JUNE 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-06-15 | Year: | 2023-2024
| Period: | 2023-06-05 | To: | 2023-06-11
|  | Total number of Interface Meters | 516
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-06-10 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
9 | ASSAM | KARIMGANJ | AM-54 | 132 kV KARIMGANJ END OF KUMARGHAT | NP-9937-A | Erroneous reading | 2023-06-06 | Till end of the week | KARIMGANJ | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
9 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
10 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 12 JUNE 23-18 JUNE 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-06-22 | Year: | 2023-2024
| Period: | 2023-06-12 | To: | 2023-06-18
|  | Total number of Interface Meters | 516
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-06-10 | 2023-06-18 | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
9 | ASSAM | KARIMGANJ | AM-54 | 132 kV KARIMGANJ END OF KUMARGHAT | NP-9937-A | Erroneous reading | 2023-06-06 | 2023-06-18 | KARIMGANJ | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
9 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
10 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 19 JUNE 23-25 JUNE 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-06-28 | Year: | 2023-2024
| Period: | 2023-06-19 | To: | 2023-06-25
|  | Total number of Interface Meters | 516
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
9 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
10 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 26 JUNE 23-02 JULY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-07-06 | Year: | 2023-2024
| Period: | 2023-06-26 | To: | 2023-07-02
|  | Total number of Interface Meters | 517
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
9 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
10 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 03 JULY 23-09 JULY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-07-13 | Year: | 2023-2024
| Period: | 2023-07-03 | To: | 2023-07-09
|  | Total number of Interface Meters | 517
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | Till end of the week | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | BTPS |  | 220 kV BTPS-ASSAM END OF NTPC LINE | NP-5318-A | Standby Meter | Weekly Drift correction required
6 | ASSAM | BTPS |  | 220 kV BTPS END OF ICT I OF NTPC | NP-9647-A | Standby Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
9 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
10 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 10 JULY 23-16 JULY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-07-20 | Year: | 2023-2024
| Period: | 2023-07-10 | To: | 2023-07-16
|  | Total number of Interface Meters | 517
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | 2023-07-20 | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
7 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
8 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
9 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 17 JULY 23-23 JULY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-07-27 | Year: | 2023-2024
| Period: | 2023-07-17 | To: | 2023-07-23
|  | Total number of Interface Meters | 517
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | Reads 33 % more | 2022-11-14 | 2023-07-20 | SANIS | Other end meter used for drawal computation; CT connectivity checking required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | ASSAM | KARIMGANJ | AM-54 | 132 kV KARIMGANJ END OF KUMARGHAT | NP-9937-A | Erroneous reading | 2023-07-21 | Till end of the week | KARIMGANJ | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
7 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
8 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
9 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 24 JULY 23-30 JULY 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-08-03 | Year: | 2023-2024
| Period: | 2023-07-24 | To: | 2023-07-30
|  | Total number of Interface Meters | 517
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM
7 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 2023-06-05 | 2023-07-30 | MIRZA
8 | ASSAM | KARIMGANJ | AM-54 | 132 kV KARIMGANJ END OF KUMARGHAT | NP-9937-A | Erroneous reading | 2023-07-21 | 2023-07-28 | KARIMGANJ
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
4 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
6 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
7 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
9 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
10 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132kV DIMAPUR(LV SIDE) ICT-2 | NP-9448-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220/132 kV DIMAPUR(HV SIDE) ICT2 | NE-0045-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR (PG) END OF KOHIMA FDR | NP-8472-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(S) II FDR | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 31 JULY 23-06 AUG 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-08-10 | Year: | 2023-2024
| Period: | 2023-07-31 | To: | 2023-08-06
|  | Total number of Interface Meters | 527
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
5 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | MIRZA | AS-93 | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 31.07.2023 | 06.08.2023 | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | POWERGRID | HAFLONG |  | 132 kV HAFLONG (PG) END OF HAFLONG (AS) | NP-8494-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
7 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
8 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
10 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | IMPHAL |  | 132 kV IMPHAL PG END OF IMPHAL FDR-I | NP-8378-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required

## 07 AUG 23-13 AUG 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-08-17 | Year: | 2023-2024
| Period: | 2023-08-07 | To: | 2023-08-13
|  | Total number of Interface Meters | 529
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | 400 kV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 07.08.2023 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | Till end of the week | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
NIL
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | AGIA |  | 131 kV AGIA-MENDIPATHAR FDR | NP-9455-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA FDR | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
9 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
10 | ASSAM | MARIANI |  | 220KV MARIANI(AS) END OF NEW MARIANI FDR | NP-9910-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
13 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
14 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
15 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
16 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | AIZAWL |  | 132 kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | HAFLONG |  | 132 kV HAFLONG (PG) END OF HAFLONG (AS) | NP-8494-A | Main Meter | Weekly Drift correction required
29 | NEEPCO | LOKTAK |  | 132 kV LOKTAK END OF RENGPANG FDR | NP-9511A | Check Meter | Weekly Drift correction required
30 | NEEPCO | AGTCCPP |  | 132 kV AGTCCPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
31 | NEEPCO | AGTCCPP |  | 133 kV AGTCCPP END OF PK BARI (TSECL) FDR 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 14 AUG 23-20 AUG 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-08-24 | Year: | 2023-2024
| Period: | 2023-08-14 | To: | 2023-08-20
|  | Total number of Interface Meters | 529
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | 400 kV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 07.08.2023 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | Till end of the week | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | POWERGRID | IMPHAL | ZZ-71 | 132/33 kV IMPHAL ICT- 1 LV SIDE | NE-0048-A | Reads 33% of HV side | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
9 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
10 | POWERGRID | NIRJULI | AR-22 | 132/33kV NIRJULI ICT-2 LV SIDE | NP-0025-A | Erroneous reading (Reads 0 value) | 14.08.2023 | Till end of the week | NIRJULI | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | AGIA |  | 131 kV AGIA-MENDIPATHAR FDR | NP-9455-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA FDR | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
9 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
10 | ASSAM | MARIANI |  | 220KV MARIANI(AS) END OF NEW MARIANI FDR | NP-9910-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
13 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
14 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
15 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
16 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | LOKTAK |  | 132 kV LOKTAK END OF RENGPANG FDR | NP-9511A | Check Meter | Weekly Drift correction required
28 | NEEPCO | AGTCCPP |  | 132 kV AGTCCPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
29 | NEEPCO | AGTCCPP |  | 133 kV AGTCCPP END OF PK BARI (TSECL) FDR 2 | NP-9456-A | Check Meter | Weekly Drift correction required

## 21 AUG 23-27 AUG 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-08-31 | Year: | 2023-2024
| Period: | 2023-08-21 | To: | 2023-08-27
|  | Total number of Interface Meters | 529
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | Till end of the week | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | 400 kV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 07.08.2023 | Till end of the week | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | Till end of the week | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | POWERGRID | IMPHAL | ZZ-71 | 132/33 kV IMPHAL ICT- 1 LV SIDE | NE-0048-A | Reads 33% of HV side | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
9 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
10 | POWERGRID | NIRJULI | AR-22 | 132/33kV NIRJULI ICT-2 LV SIDE | NP-0025-A | Erroneous reading (Reads 0 value) | 14.08.2023 | Till end of the week | NIRJULI | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | AGIA |  | 131 kV AGIA-MENDIPATHAR FDR | NP-9455-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA FDR | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
9 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
10 | ASSAM | MARIANI |  | 220KV MARIANI(AS) END OF NEW MARIANI FDR | NP-9910-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
13 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
14 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
15 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
16 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | LOKTAK |  | 132 kV LOKTAK END OF RENGPANG FDR | NP-9511A | Check Meter | Weekly Drift correction required
28 | NEEPCO | AGTCCPP |  | 132 kV AGTCCPP END OF AGARTALA-1 FDR | NP-9081-A | Main Meter | Weekly Drift correction required
29 | NEEPCO | AGTCCPP |  | 133 kV AGTCCPP END OF PK BARI (TSECL) FDR 2 | NP-9456-A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | MARIANI | Time drift report not received
2 | POWERGRID | ZIRO | Time drift report not received
3 | POWERGRID | SALAKATI | Time drift report not received
4 | POWERGRID | BONGAIGAON | Time drift report not received
5 | POWERGRID | KUMARGHAT | Time drift report not received

## 28 AUG 23-03 SEPT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-09-07 | Year: | 2023-2024
| Period: | 2023-08-28 | To: | 2023-09-03
|  | Total number of Interface Meters | 529
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | PANCHGRAM | AS-06 | 132 kV PANCHGRAM END OF LUMSHNONG FDR | NP-7595-A | Reads 0 value | 2023-05-29 | 03.09.2023 | PANCHGRAM | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | MIRZA | AS-93 | 400 kV MIRZA END OF SILCHAR FDR | NP-9981-A | Erroneous reading, sign reversal | 07.08.2023 | 28.08.2023 | MIRZA | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | Till end of the week | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
8 | POWERGRID | IMPHAL | ZZ-71 | 132/33 kV IMPHAL ICT- 1 LV SIDE | NE-0048-A | Reads 33% of HV side | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
9 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
10 | POWERGRID | NIRJULI | AR-22 | 132/33kV NIRJULI ICT-2 LV SIDE | NP-0025-A | Erroneous reading (Reads 0 value) | 14.08.2023 | 30.08.2023 | NIRJULI | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | AGIA |  | 131 kV AGIA-MENDIPATHAR FDR | NP-9455-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA FDR | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
9 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
10 | ASSAM | MARIANI |  | 220KV MARIANI(AS) END OF NEW MARIANI FDR | NP-9910-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
13 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
14 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
15 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
16 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | MARIANI | Time drift report not received
3 | POWERGRID | SALAKATI | Time drift report not received
4 | POWERGRID | BONGAIGAON | Time drift report not received
5 | POWERGRID | KUMARGHAT | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | BALIPARA | Data received on 06.09.2023
2 | NEEPCO | DOYANG | Data received on 06.09.2023
5 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
3 | MANIPUR | TIPAIMUKH | Data not received due to ethnic issue and internet issue. Put up in 204th OCCM
4 | MANIPUR | THOUBAL
6 | MANIPUR | KARONG
7 | MIZORAM | LUNGMUAL | Data not received. Mail sent to concerned
8 | TRIPURA | UDAIPUR | Data not received. Put up in 204th OCCM

## 04 SEPT 23-10 SEPT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-09-14 | Year: | 2023-2024
| Period: | 2023-09-04 | To: | 2023-09-10
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | Till end of the week | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | POWERGRID | IMPHAL | ZZ-71 | 132/33 kV IMPHAL ICT- 1 LV SIDE | NE-0048-A | Reads 33% of HV side | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
6 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA FDR | NP-9920-A | Main Meter | Weekly Drift correction required
7 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
8 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
9 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
10 | ASSAM | MARIANI |  | 220KV MARIANI(AS) END OF NEW MARIANI FDR | NP-9910-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
13 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
14 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
15 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
16 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II LV SIDE | NP-9959-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF KATHALAGURI | NE-0034-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI |  | 220 kV MARIANI(PG) END OF MOKOKCHANG-2 | NP-9911-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-2 | NP-9954-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI END OF MISA CKT-1 | NP-9952-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI |  | 400/220 kV NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400 kV NEW MARIANI- NEW KOHIMA (KMTL)-1 | NP-9974-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | KUMARGHAT |  | 132 kV K'GHAT (PG) END OF KARIMGANJ FEEDER | NP-6862-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | MARIANI | Time drift report not received
2 | POWERGRID | SALAKATI | Time drift report not received
3 | POWERGRID | NIRJULI | Time drift report not received
4 | POWERGRID | BONGAIGAON | Time drift report not received
5 | POWERGRID | KUMARGHAT | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | MARIANI | Data received on 13.09.2023
2 | MEGHALAYA | UMTRU
3 | MANIPUR | THOUBAL
4 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
5 | MANIPUR | KARONG | Data not received. Put up in 204th OCCM
6 | MANIPUR | TIPAIMUKH
7 | MANIPUR | KARONG
8 | MIZORAM | LUNGMUAL | Data not received. Mail sent to concerned
9 | TRIPURA | UDAIPUR | Data not received. Put up in 204th OCCM

## 11 SEPT 23-17 SEPT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-09-21 | Year: | 2023-2024
| Period: | 2023-09-11 | To: | 2023-09-17
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | Till end of the week | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | AGIA |  | 132 kV AGIA-NANGALBIBRA FDR | NP-9920-A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
7 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
8 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
9 | ASSAM | MARIANI |  | 220KV MARIANI(AS) END OF NEW MARIANI FDR | NP-9910-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
12 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR-I | NE-0088-A | Main Meter | Weekly Drift correction required
13 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
14 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
15 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (STERLITE) | NP-9919-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | BONGAIGAON | Time drift report not received
2 | MIZORAM | LUNGMUAL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | ARUNACHAL PRADESH | DEOMALI | Data received on 20.09.2023
2 | TRIPURA | UDAIPUR
3 | ASSAM | MIRZA
4 | ASSAM | KAHILIPARA
5 | NEEPCO | KOPILI
6 | NEEPCO | KAMENG
7 | POWERGRID | RANGIA
8 | POWERGRID | BALIPARA
9 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
10 | MANIPUR | KARONG | Data not received. Put up in 204th OCCM
11 | MANIPUR | YUREMBAM
12 | MANIPUR | NINGTHOUKHONG
13 | MANIPUR | THOUBAL
14 | MANIPUR | TIPAIMUKH
15 | MIZORAM | LUNGMUAL | Data not received. Mail sent to concerned

## 18 SEPT 23-24 SEPT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-09-28 | Year: | 2023-2024
| Period: | 2023-09-18 | To: | 2023-09-24
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | Till end of the week | MELRIAT | Meter replacement required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | Till end of the week | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
6 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
7 | ASSAM | MARIANI |  | 220 kV MARIANI-KATHALGURI FDR | NP-6888-A | Main Meter | Weekly Drift correction required
8 | ASSAM | MARIANI |  | 220KV MARIANI(AS) END OF NEW MARIANI FDR | NP-9910-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
12 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
13 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
14 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
15 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (INDIGRID) | NP-9919-A | Standby Meter | Weekly Drift correction required
16 | TRIPURA | DHARMANAGAR |  | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Main Meter | Weekly Drift correction required
17 | POWERGRID | KUMARGHAT |  | 132 kV KUMARGHAT END OF KARIMGANJ FDR | NP-6862-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | KUMARGHAT |  | 133 kV KUMARGHAT END OF AIZAWL FDR | NP-6861-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | NTPC | BGTPP | Data received on 27.09.2023
2 | MEGHALAYA | UMTRU
3 | MIZORAM | KOLASIB
4 | POWERGRID | BONGAIGAON
5 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
6 | MIZORAM | LUNGMUAL | Data not received. Mail sent to concerned
7 | ARUNACHAL PRADESH | DEOMALI | Data not received. Mail sent to concerned

## 25 SEPT 23-01 OCT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-10-05 | Year: | 2023-2024
| Period: | 2023-09-25 | To: | 2023-10-01
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2022-03-07 | 2023-10-01 | MELRIAT | Meter replaced
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | ASSAM | GOHPUR | AS-13 | 132 kV GOHPUR END OF NIRJULI FDR | NP-9688-A | Erroneous reading | 07.08.2023 | 28.09.2023 | GOHPUR | Other end meter used for drawal computation; CT/PT connectivity checking required
7 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
6 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
11 | NAGALAND | DIMAPUR |  | 132 kV DIMAPUR(S)END OF DIMAPUR(PG) I LINE | NP-5777-A | Standby Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV P'KANCHANBARI END OF K'GHAT(PG) FDR | NP-6875-A | Standby Meter | Weekly Drift correction required
13 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (INDIGRID) | NP-9919-A | Standby Meter | Weekly Drift correction required
14 | TRIPURA | DHARMANAGAR |  | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Main Meter | Weekly Drift correction required
15 | POWERGRID | KUMARGHAT |  | 132 kV KUMARGHAT END OF KARIMGANJ FDR | NP-6862-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | KUMARGHAT |  | 133 kV KUMARGHAT END OF AIZAWL FDR | NP-6861-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | NTPC | BGTPP | Data received on 04.10.2023
2 | NEEPCO | KOPILI
3 | POWERGRID | BALIPARA
4 | POWERGRID | BONGAIGAON
5 | POWERGRID | NIRJULI
6 | ASSAM | PAILAPOOL
7 | ASSAM | SAMAGURI
8 | ASSAM | MIRZA
9 | ASSAM | PAVOI
10 | MIZORAM | KOLASIB
11 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
12 | MANIPUR | KARONG | Data not received. Mail sent to concerned
13 | MANIPUR | THOUBAL
14 | MANIPUR | TIPAIMUKH
15 | MIZORAM | LUNGMUAL
16 | ARUNACHAL PRADESH | DEOMALI | Data not received. Mail sent to concerned

## 02 OCT 23-08 OCT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-10-12 | Year: | 2023-2024
| Period: | 2023-10-02 | To: | 2023-10-08
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2023-10-04 | Till end of the week | MELRIAT | Meter replaced, issue still persisting ; CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | POWERGRID | DIMAPUR | NG-07 | 220 kV DIMAPUR END OF MISA-2 FDR | NP-9452-A | Reads approx 95% less, sign reversal | 2023-04-03 | 02.10.2023 | DIMAPUR | Meter replaced
4 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
6 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
7 | ASSAM | MIRZA |  | 400 kV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
11 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (INDIGRID) | NP-9919-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220kV MISA END OF SAMAGURI 1 | NP-9501-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MISA |  | 220kV MISA END OF SAMAGURI 2 | NP-9501-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MISA |  | 400/220KV MISA ICT-2 LV SIDE | NE-0008-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | MISA |  | 400/220KV MISA ICT-3 HV SIDE | NP-9401-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | 400kV MISA END OF BALIPARA 2 | NP-5291-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | MISA |  | 400kV MISA END OF NEW MARIANI 1 | NP-9892-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | MISA |  | 400kV MISA END OF NEW MARIANI 2 | NP-9894-A | Line Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | NTPC | BGTPP | Data received on 11.10.2023
2 | NEEPCO | KOPILI
3 | POWERGRID | MARIANI
4 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
5 | MANIPUR | KARONG | Data not received. Mail sent to concerned
6 | MANIPUR | THOUBAL
7 | MANIPUR | TIPAIMUKH

## 09 OCT 23-15 OCT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-10-19 | Year: | 2023-2024
| Period: | 2023-10-09 | To: | 2023-10-15
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2023-10-04 | Till end of the week | MELRIAT | Meter replaced, issue still persisting ; CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 15% less, sign reversal | 2023-04-03 | Till end of the week | DIMAPUR | Meter replacement required
3 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
4 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSOO |  | 132 kV UMRANGSOO END OF KHLEIRIAT | NP-5290-A | Standby Meter | Meter replacemnet required
5 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
6 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
7 | ASSAM | MIRZA |  | 400 kV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
11 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
12 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (INDIGRID) | NP-9919-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220kV MISA END OF SAMAGURI 1 | NP-9501-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MISA |  | 220kV MISA END OF SAMAGURI 2 | NP-9501-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MISA |  | 400/220KV MISA ICT-2 LV SIDE | NE-0008-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | MISA |  | 400/220KV MISA ICT-3 HV SIDE | NP-9401-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | 400kV MISA END OF BALIPARA 2 | NP-5291-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | MISA |  | 400kV MISA END OF NEW MARIANI 1 | NP-9892-A | Line Meter | Weekly Drift correction required
23 | POWERGRID | MISA |  | 400kV MISA END OF NEW MARIANI 2 | NP-9894-A | Line Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MANIPUR | NINGTHOUKHONG | Data received on 18.10.2023
2 | POWERGRID | BONGAIGAON
3 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
4 | MANIPUR | KARONG | Data not received. Mail sent to concerned
5 | MANIPUR | THOUBAL
6 | MANIPUR | TIPAIMUKH

## 16 OCT 23-22 OCT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-10-26 | Year: | 2023-2024
| Period: | 2023-10-16 | To: | 2023-10-22
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | MELRIAT | MZ-19 | 132 KV MELRIAT END OF SILCHAR-I FDR | NP-9557-A | Reads twice | 2023-10-04 | Till end of the week | MELRIAT | Meter replaced, issue still persisting ; CT/PT connectivity checking required
2 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 12% less, sign reversal | 2023-10-16 | Till end of the week | DIMAPUR | Meter replaced, issue still persisting ; CT/PT connectivity checking required
3 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
4 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
5 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
6 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
6 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
7 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | TENGA |  | 132 kV TENGA- BALIPARA FDR | NP-9696-A | Main Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | TENGA |  | 133 kV TENGA- BALIPARA FDR | NP-9698-A | Check Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
6 | ASSAM | MIRZA |  | 400 kV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR I | NP-9706-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
11 | TRIPURA | P'K BARI |  | 132 kV PK BARI (TSECL) END OF PK BARI (INDIGRID) | NP-9919-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 220kV MISA END OF SAMAGURI 1 | NP-9501-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220kV MISA END OF SAMAGURI 2 | NP-9501-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MISA |  | 400/220KV MISA ICT-2 LV SIDE | NE-0008-A | Line Meter | Weekly Drift correction required
19 | POWERGRID | MISA |  | 400/220KV MISA ICT-3 HV SIDE | NP-9401-A | Line Meter | Weekly Drift correction required
20 | POWERGRID | MISA |  | 400kV MISA END OF BALIPARA 2 | NP-5291-A | Line Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | 400kV MISA END OF NEW MARIANI 1 | NP-9892-A | Line Meter | Weekly Drift correction required
22 | POWERGRID | MISA |  | 400kV MISA END OF SILCHAR 2 | NP-9929-A | Line Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
5 | POWERGRID | HAFLONG | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | BONGAIGAON | Received on 25.10.2023
2 | POWERGRID | DIMAPUR
3 | POWERGRID | MARIANI
4 | POWERGRID | KUMARGHAT
5 | POWERGRID | BALIPARA
6 | POWERGRID | MISA
7 | POWERGRID | RANGIA
8 | POWERGRID | AIZAWL
9 | POWERGRID | SALAKATI
10 | POWERGRID | NIRJULI
11 | ASSAM | AGIA
12 | ASSAM | AZARA
13 | ASSAM | KAHILIPARA
14 | ASSAM | SARUSAJAI
15 | ASSAM | MARIANI AS
16 | TRIPURA | UDAIPUR
17 | MEGHALAYA | UMTRU
18 | MEGHALAYA | KHLEIHRIAT
19 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
20 | MANIPUR | KARONG | Data not received. Mail sent to concerned
21 | MANIPUR | TIPAIMUKH

## 23 OCT 23-29 OCT 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-11-02 | Year: | 2023-2024
| Period: | 2023-10-23 | To: | 2023-10-29
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 12% less, sign reversal | 2023-10-16 | Till end of the week | DIMAPUR | Meter replaced, issue still persisting ; CT/PT connectivity checking required
2 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
4 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
5 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | PAILAPOOL | AS-10 | 132 kV PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | High time drift | 2023-08-21 | Till end of the week | PAILAPOOL | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
6 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
7 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-II FDR | NP-8801-A | Main Meter | Weekly Drift correction required
3 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | MISA |  | 400kV MISA END OF BALIPARA 2 | NP-5291-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | MISA |  | 400kV MISA END OF NEW MARIANI 1 | NP-9892-A | Line Meter | Weekly Drift correction required
14 | POWERGRID | MISA |  | 400kV MISA END OF SILCHAR 2 | NP-9929-A | Line Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | BONGAIGAON | Received on 01.11.2023
2 | POWERGRID | BALIPARA
3 | ASSAM | GOHPUR
4 | NTPC | BGTPP
5 | ARUNACHAL | TENGA
6 | OTPC | PALATANA | Received on 02.11.2023
7 | MANIPUR | RENGPANG | Data not received due to DCD issue. Put up in 200th OCCM
8 | MANIPUR | KARONG | Data not received. Mail sent to concerned
9 | MANIPUR | TIPAIMUKH
10 | TRIPURA | BUDHJUNGNAGAR

## 30 OCT 23-05 NOV 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-11-09 | Year: | 2023-2024
| Period: | 2023-10-30 | To: | 2023-11-05
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 12% less, sign reversal | 2023-10-16 | Till end of the week | DIMAPUR | Meter replaced, issue still persisting ; CT/PT connectivity checking required
2 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
4 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
5 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | MISA |  | 400kV MISA END OF BALIPARA 2 | NP-5291-A | Line Meter | Weekly Drift correction required
12 | POWERGRID | MISA |  | 400kV MISA END OF NEW MARIANI 1 | NP-9892-A | Line Meter | Weekly Drift correction required
13 | POWERGRID | MISA |  | 400kV MISA END OF SILCHAR 2 | NP-9929-A | Line Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BALIPARA | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | MARIANI | Received on 08.11.2023
2 | NEEPCO | AGBPP
3 | MANIPUR | NINGTHOUKHONG
4 | MEGHALAYA | UMTRU
5 | MEGHALAYA | BYNIHAT
6 | MIZORAM | KOLASIB
7 | MANIPUR | RENGPANG | Data not received. Mail sent to concerned
8 | MANIPUR | KARONG
9 | MANIPUR | TIPAIMUKH
10 | TRIPURA | UDAIPUR
11 | TRIPURA | AMBASSA
12 | TRIPURA | BUDHJUNGNAGAR

## 06 NOV 23-12 NOV 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-11-16 | Year: | 2023-2024
| Period: | 2023-11-06 | To: | 2023-11-12
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | DIMAPUR | NG-06 | 220 kV DIMAPUR END OF MISA-1 FDR | NP-9673-A | Reads approx 12% less, sign reversal | 2023-10-16 | 2023-11-11 | DIMAPUR | Meter replaced
2 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
4 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
5 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
6 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-11-06 | 2023-11-11 | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
7 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BALIPARA | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | BONGAIGOAN | Received on 16.11.2023
2 | TRIPURA | UDAIPUR | Received on 15.11.2023
3 | MANIPUR | YUREMBAM
4 | ASSAM | KAHELIPARA
5 | KMTL | NEW KOHIMA
6 | MANIPUR | RENGPANG | Put up in 207th OCCM
7 | MANIPUR | TIPAIMUKH
8 | TRIPURA | BUDHJUNGNAGAR
9 | MIZORAM | LUNGMUAL

## 13 NOV 23-19 NOV 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-11-23 | Year: | 2023-2024
| Period: | 2023-11-13 | To: | 2023-11-19
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
4 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-11-13 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | AZARA | AS-93 | 400 kV AZARA END OF SILCHAR END | NP-9981-A | Erroneous reading | 2023-11-15 | Till end of the week | AZARA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG) FDR II | NP-9603-A | Standby Meter | Weekly Drift correction required
7 | MEGHALAYA | KAHELIPARA |  | 132 kV KAHELIPARA END OF UMTRU FDR I | NE-0088-A | Main Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BALIPARA | Time drift report not received
3 | POWERGRID | BONGAIGAON | Time drift report not received
4 | TRIPURA | UDAIPUR | Time drift report not received
5 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | SALAKATI | Received on 22.11.2023
2 | POWERGRID | JIRIBAM
3 | NTPC | BGTPP
4 | POWERGRID | AIZAWL | Received on 23.11.2023
5 | MANIPUR | RENGPANG | Put up in 207th OCCM
6 | TRIPURA | BUDHJUNGNAGAR
7 | MIZORAM | LUNGMUAL | Mail sent to concerned

## 20 NOV 23-26 NOV 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-11-30 | Year: | 2023-2024
| Period: | 2023-11-20 | To: | 2023-11-26
|  | Total number of Interface Meters | 531
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
4 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-11-13 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | AZARA | AS-93 | 400 kV AZARA END OF SILCHAR END | NP-9981-A | Erroneous reading | 2023-11-15 | Till end of the week | AZARA | Other end meter used for drawal computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | KAHILIPARA |  | 132 kV KAHILIPRA END OF UMTRU-1 FEEDER | NE-0088-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG) FDR II | NP-9603-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | UDAIPUR | Received on 30.11.2023
2 | MIZORAM | KOLASIB | Received on 29.11.2023
3 | NTPC | BGTPP
4 | POWERGRID | AIZAWL
5 | ASSAM | MARIANI
5 | MANIPUR | RENGPANG | Put up in 207th OCCM
6 | TRIPURA | BUDHJUNGNAGAR
7 | MIZORAM | LUNGMUAL | Mail sent to concerned

## 27 NOV 23-03 DEC 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-12-07 | Year: | 2023-2024
| Period: | 2023-11-27 | To: | 2023-12-03
|  | Total number of Interface Meters | 533
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
4 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-11-13 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | ASSAM | AZARA | AS-93 | 400 kV AZARA END OF SILCHAR END | NP-9981-A | Erroneous reading | 2023-11-15 | 2023-12-01 | AZARA | Data seems to be correct since 01-12-2023.
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | KAHILIPARA |  | 132 kV KAHILIPRA END OF UMTRU-1 FEEDER | NE-0088-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG) FDR II | NP-9603-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | UDAIPUR | Received on 07.12.2023
4 | ARUNACHAL PRADESH | CHIMPU | Received on 06.12.2023
5 | ASSAM | TINSUKIA
6 | TRIPURA | BUDHJUNGNAGAR | Put up in 207th OCCM
5 | MANIPUR | RENGPANG | Mail sent to concerned
7 | MIZORAM | LUNGMUAL

## 04 DEC 23-10 DEC 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-12-14 | Year: | 2023-2024
| Period: | 2023-12-04 | To: | 2023-12-10
|  | Total number of Interface Meters | 533
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
4 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-11-13 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (STERLITE) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | KAHILIPARA |  | 132 kV KAHILIPRA END OF UMTRU-1 FEEDER | NE-0088-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG) FDR II | NP-9603-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MANIPUR | TIPAIMUKH | Received on 13.12.2023
2 | MANIPUR | YUREMBAM
3 | TRIPURA | UDAIPUR | Mail sent to concerned
4 | MIZORAM | LUNGMUAL | Mail sent to concerned

## 11 DEC 23-17 DEC 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-12-21 | Year: | 2023-2024
| Period: | 2023-12-11 | To: | 2023-12-17
|  | Total number of Interface Meters | 533
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
4 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-11-13 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (STERLITE) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | KAHILIPARA |  | 132 kV KAHILIPRA END OF UMTRU-1 FEEDER | NE-0088-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG) FDR II | NP-9603-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
3 | TRIPURA | UDAIPUR | Received on 20.12.2023
4 | MIZORAM | LUNGMUAL | Not Received. Mailed to concerened
| MEGHALAYA | KHLIERIAT | Received on 20.12.2023
| NAGALAND | SANIS | Received on 20.12.2023
| MANIPUR | RENGPANG | Data conversion error
| TRIPURA | BUDHJUNGNAGAR | Not Received. Mailed to concerened
| TRIPURA | AMBASSA | Not Received. Mailed to concerened
| POWERGRID | BONGAIGAON | Received on 20.12.2023
| POWERGRID | JIRIBAM | Received on 20.12.2023

## 18 DEC 23-24 DEC 2023
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2023-12-28 | Year: | 2023-2024
| Period: | 2023-12-18 | To: | 2023-12-24
|  | Total number of Interface Meters | 533
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Reads 75 % less | 2023-04-03 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF KAMENG-2 FDR | NP-9612-A | Reads 75 % less | 2023-10-02 | Till end of the week | BALIPARA | Other end meter used for injection computation; CT/PT connectivity checking required
4 | TRIPURA | AMBASSA | TR-26 | 132 kV AMBASSA(TSECL) end of PK BARI (STERLITE) | NP-9990-B | Sign Reversal | 2023-10-16 | Till end of the week | AMBASSA | Other end meter used for injection computation; CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAV FDR | NP-6892-B | Erroneous reading | 2023-11-13 | Till end of the week | DHARMANAGAR | Other end meter used for drawal computation; CT/PT connectivity checking required
6 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (STERLITE) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-19 | 132 kV KOHIMA END OF DIMAPUR(PG) FDR | NP-9699-A | High time drift | 2023-08-14 | Till end of the week | KOHIMA | Other end meter used for drawal computation; time drift corrective action required
2 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | BONGAIGAON | AS-25 | 400 kV BONGAIGAON END OF BINAGURI-1 FEEDER | NP-8468-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
4 | POWERGRID | BONGAIGAON | AS-26 | 400 kV BONGAIGAON END OF BINAGURI-2 FEEDER | NP-8469-A | High time drift | 2023-09-18 | Till end of the week | BONGAIGAON | Other end meter used for drawal computation; time drift corrective action required
5 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
6 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | Till end of the week | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | KAHILIPARA |  | 132 kV KAHILIPRA END OF UMTRU-1 FEEDER | NE-0088-A | Main Meter | Weekly Drift correction required
4 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR III | NP-9706-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | IMPHAL |  | 132 kV IMPHAL(MAN) END OF IMPHAL(PG) FDR II | NP-9546-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG) FDR II | NP-9603-A | Standby Meter | Weekly Drift correction required
8 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR I | NP-9072-A | Main Meter | Weekly Drift correction required
9 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF ALIPURDUAR FDR II | NP-9069-A | Main Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-1 | NP-9476-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 400 kV BONGAIGAON END OF NTPC_BgTPP-2 | NP-9477-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | POWERGRID | BONGAIGAON | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | POWERGRID | AIZAWL | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | MARIANI | Received on 27.12.2023
2 | POWERGRID | SALAKATI
3 | POWERGRID | RANGIA
4 | POWERGRID | SILCHAR
5 | POWERGRID | JIIRBAM
6 | MIZORAM | KOLASIB
7 | ASSAM | PAILAPOOL
8 | ASSAM | SARUSAJAI
9 | ASSAM | AGIA
10 | ASSAM | PAVOI
11 | NTPC | BGTPP
12 | TRIPURA | BUDHJUNGNAGAR | Not Received. Mailed to concerened
13 | TRIPURA | AMBASSA | Not Received. Mailed to concerened