## 01 APR 24-07 APR 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-04-11 | Year: | 2024-2025
| Period: | 2024-04-01 | To: | 2024-04-07
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading (close to 0) | 2024-04-01 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
4 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | UMRANGSHO | AM-04 | 132 kV UMRANGSHO END OF KHANDONG | NP-5290-A | High time drift | 2023-10-16 | 2024-04-01 | UMRANGSHO | Other end meter used for drawal computation; meter replacement required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | KAHILIPARA |  | 132 kV KAHILIPRA END OF UMTRU-1 FEEDER | NE-0088-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL(PG) FDR II | NP-9603-A | Standby Meter | Weekly Drift correction required
7 | NEEPCO | AgGBPS |  | HV SIDE OF GT OF STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
8 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | LOKTAK UNIT#2 | NP-9047-A | Standby meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-01 | NP-5809-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | MISA |  | 400 kV SIDE OF MISA ICT-1 | NP-5300-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | IMPHAL |  | 132kV IMPHAL PG END OF IMPHAL I | NP-8378-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | NIRJULI |  | 132/33 kV ICT-II HV SIDE | NP-9662-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | NIRJULI |  | 132kV NIRJULI END OF LEKHI FDR | NP-9664-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | MEGHALAYA | KILLING | Time drift report not received
5 | ASSAM | MARIANI | Time drift report not received
6 | TRIPURA | UDAIPUR | Time drift report not received
7 | NEEPCO | DOYANG | Time drift report not received
8 | NEEPCO | AGBPP | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | POWERGRID | ROING | Time drift report not received
11 | POWERGRID | AIZAWL | Time drift report not received
12 | POWERGRID | HAFLONG | Time drift report not received
13 | POWERGRID | SILCHAR | Time drift report not received
14 | POWERGRID | MARIANI | Time drift report not received
15 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MANIPUR | THOUBAL | Received on 10-04-2024
2 | MANIPUR | YUREMBAM
3 | MANIPUR | TIPAIMUKH
4 | POWERGRID | DIMAPUR | Received on 10-04-2024. DCD issue stated
5 | POWERGRID | KHLEIHRIAT | Not Received for meter no. NP-6883-A. Mailed to concerened
6 | TRIPURA | AMBASSA | Not Received. Mailed to concerened

## 08 APR 24-14 APR 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-04-18 | Year: | 2024-2025
| Period: | 2024-04-08 | To: | 2024-04-14
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading (close to 0) | 2024-04-01 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
4 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | KAHILIPARA |  | 132 kV KAHILIPRA END OF UMTRU-1 FEEDER | NE-0088-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
4 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
7 | NEEPCO | AgGBPS |  | HV SIDE OF GT OF STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
8 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | LOKTAK UNIT#2 | NP-9047-A | Standby meter | Weekly Drift correction required
11 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-01 | NP-5809-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | DIMAPUR |  | 132kV DIMAPUR(PG) END OF DIMAPUR(ST) FDR-02 | NP-9649-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | MISA |  | 400 kV SIDE OF MISA ICT-1 | NP-5300-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | IMPHAL |  | 132kV IMPHAL PG END OF IMPHAL I | NP-8378-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | NIRJULI |  | 132/33 kV ICT-II HV SIDE | NP-9662-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | NIRJULI |  | 132kV NIRJULI END OF LEKHI FDR | NP-9664-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | TRIPURA | UDAIPUR | Time drift report not received
5 | NEEPCO | DOYANG | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | KHANDONG | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | BALIPARA | Time drift report not received
11 | POWERGRID | IMPHAL | Time drift report not received
12 | POWERGRID | BNC | Time drift report not received
13 | POWERGRID | SILCHAR | Time drift report not received
14 | POWERGRID | MARIANI | Time drift report not received
15 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | ZIRO | Received on 17-04-2024
2 | ASSAM | KAHELIPARA
3 | TRIPURA | AMBASSA | Not Received. Mailed to concerened

## 15 APR 24-21 APR 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-04-25 | Year: | 2024-2025
| Period: | 2024-04-15 | To: | 2024-04-21
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading (close to 0) | 2024-04-01 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
4 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-1 FEEDER | NP-9680-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | ASSAM | HAILAKANDI |  | 132 kV HAILAKANDI END OF SILCHAR 1 FDR | NP-5301-A | Main Meter | Weekly Drift correction required
5 | ASSAM | SARUSAJAI |  | 132 kV SARUSAJAI END OF UMTRU II FDR | NP-9922-A | Main Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | KARONG |  | 132 kV KARONG END OF KOHIMA FDR | NP-9667-A | Main Meter | Weekly Drift correction required
8 | NEEPCO | AgGBPS |  | HV SIDE OF GT OF STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | LOKTAK UNIT#2 | NP-9047-A | Standby meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 400 kV SIDE OF MISA ICT-1 | NP-5300-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | IMPHAL |  | 132kV IMPHAL PG END OF IMPHAL I | NP-8378-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | MEGHALAYA | UMTRU | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | DOYANG | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | PANYOR LOWER | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | STERLITE | NORTH LAKHIMPUR | Time drift report not received
11 | POWERGRID | ROING | Time drift report not received
12 | POWERGRID | AIZAWL | Time drift report not received
13 | POWERGRID | IMPHAL | Time drift report not received
14 | POWERGRID | BNC | Time drift report not received
15 | POWERGRID | SILCHAR | Time drift report not received
16 | POWERGRID | MARIANI | Time drift report not received
17 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | RANGIA | Received on 24-04-2024
2 | MANIPUR | KARONG
3 | MIZORAM | KOLASIB
5 | TRIPURA | AMBASSA | Not Received. Mailed to concerened

## 22 APR 24-28 APR 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-05-02 | Year: | 2024-2025
| Period: | 2024-04-22 | To: | 2024-04-28
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading (close to 0) | 2024-04-01 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
4 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-1 FEEDER | NP-9680-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | SARUSAJAI |  | 132 kV SARUSAJAI END OF UMTRU II FDR | NP-9922-A | Main Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
8 | NEEPCO | AgGBPS |  | HV SIDE OF GT OF STG-2 | NP-9082-A | Standby Meter | Weekly Drift correction required
8 | NEEPCO | KOPILI |  | HV SIDE OF GT OF UNIT 4 | NE-0123-A | Standby Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 400 kV SIDE OF MISA ICT-1 | NP-5300-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 220 kV SIDE OF MISA ICT-2 | NE-0008-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 1 | NE-0043-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 2 | NE-0047-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 3 | NE-0044-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF MISA 1 | NE-0036-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BNC 2 | NP-9483-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | NAGALAND | SANIS | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | DOYANG | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | PANYOR LOWER | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | STERLITE | NORTH LAKHIMPUR | Time drift report not received
11 | POWERGRID | ROING | Time drift report not received
12 | POWERGRID | AIZAWL | Time drift report not received
13 | POWERGRID | SILCHAR | Time drift report not received
14 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | POWERGRID | RANGIA | Received on 01-05-2024
2 | INDIGRID | PK BARI | Received on 01-05-2024(Issue with Optical Cable stated)
3 | MANIPUR | THOUBAL | Not Received. Mailed to concerened
4 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
5 | TRIPURA | AMBASSA | Not Received. Mailed to concerened

## 29 APR 24-05 MAY 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-05-09 | Year: | 2024-2025
| Period: | 2024-04-29 | To: | 2024-05-05
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading (close to 0) | 2024-04-01 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
4 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 50%) | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
6 | OTPCL | PALATANA | PL-02/ PL-17 | 400 kV PALATANA END OF SILCHAR II | NP-0010-A/ NP-9560-A | Erratic Reading (Around 50%) | 29-04-2024 (11:45 Hrs) | 29-04-2024 (13:00 Hrs) | - | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-1 FEEDER | NP-9680-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | SARUSAJAI |  | 132 kV SARUSAJAI END OF UMTRU II FDR | NP-9922-A | Main Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | AIZAWL |  | 132kV AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 400 kV MISA END OF SILCHAR II | NP-9929-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 220 kV SIDE OF MISA ICT-2 | NE-0008-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 1 | NE-0043-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 2 | NE-0047-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 3 | NE-0044-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF MISA 1 | NE-0036-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 400/220 kV ICT#2 (HV) SIDE | NP-5811-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | MEGHALAYA | LUMSHNONG | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | TRIPURA | UDAIPUR | Time drift report not received
7 | NEEPCO | DOYANG | Time drift report not received
8 | NEEPCO | AGBPP | Time drift report not received
9 | NEEPCO | PANYOR LOWER | Time drift report not received
10 | NTPC | BGTPP | Time drift report not received
11 | POWERGRID | ROING | Time drift report not received
12 | POWERGRID | AIZAWL | Time drift report not received
13 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MANIPUR | TIPAIMUKH | Received on 08-05-2024
2 | MIZORAM | LUANGMUAL | Received on 08-05-2024
3 | TRIPURA | AMBASSA | Not Received. Mailed to concerened

## 06 MAY 24-12 MAY 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-05-16 | Year: | 2024-2025
| Period: | 2024-05-06 | To: | 2024-05-12
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading (close to 0) | 2024-04-01 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
4 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 50%) | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
8 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
10 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
11 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA I | NP-5299-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | MISA |  | 400 kV MISA END OF SILCHAR II | NP-9929-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
16 | MEGHALAYA | NANGALBIBRA |  | 132kV AGIA-NANGALBIBRA | NP-9945-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV SIDE OF MISA ICT-2 | NE-0008-A | Standby Meter | Weekly Drift correction required
18 | INDIGRID | SM NAGAR |  | 132kV SM NAGAR(ISTS) END OF SM NAGAR(TSECL) | NP-9942-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 4 | NE-0005-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | NAGALAND | SANIS | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | DOYANG | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | NAGALAND | KOHIMA | Time drift report not received
10 | POWERGRID | SILCHAR | Time drift report not received
11 | ARUNACHAL | TENGA | Time drift report not received
12 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | NAGALAND | KOHIMA | Received on 15-05-2024
3 | ASSAM | KAHELIPARA | Received on 15-05-2024
4 | ASSAM | PAILAPOOL | Received on 15-05-2024

## 13 MAY 24-19 MAY 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-05-23 | Year: | 2024-2025
| Period: | 2024-05-13 | To: | 2024-05-19
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG FDR | NP-9947-A | Erroneous reading (close to 0) | 2024-04-01 | Till end of the week | KOHIMA | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
3 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
4 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
5 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 50%) | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | NANGALBIBRA |  | 132kV AGIA-NANGALBIBRA | NP-9945-A | Main Meter | Weekly Drift correction required
8 | NEEPCO | AgGBPS |  | 132KV AgGBPS END OF AGARTALA FDR 1 | NP-9081-A | Main Meter | Weekly Drift correction required
9 | NEEPCO | AgGBPS |  | 132KV AgGBPS END OF AGARTALA FDR 1 | NP-9513-A | Check Meter | Weekly Drift correction required
10 | NEEPCO | AgGBPS |  | 132KV AgGBPS END OF AGARTALA FDR 2 | NP-9093-A | Main Meter | Weekly Drift correction required
11 | NEEPCO | AgGBPS |  | 132KV AgGBPS END OF AGARTALA FDR 2 | NP-9514-A | Check Meter | Weekly Drift correction required
12 | NEEPCO | AgGBPS |  | 132 kV AGTPP END OF PK BARI (TSECL)- 1 | NP-9457-A | Check Meter | Weekly Drift correction required
13 | NEEPCO | AgGBPS |  | 132 kV AGTPP END OF PK BARI (TSECL)- 2 | NP-9456-A | Check Meter | Weekly Drift correction required
14 | NEEPCO | KOPILI |  | HV SIDE OF GT OF UNIT 4 | NE-0123-A | Standby Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
16 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
17 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
18 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MISA |  | 220 kV SIDE OF MISA ICT-2 | NE-0008-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | BALIPARA |  | 400 KV BALIPARA END OF BONGAIGAON 4 | NE-0005-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | ARUNACHAL | TENGA | Time drift report not received
2 | MIZORAM | LUNGMUAL | Time drift report not received
3 | MIZORAM | KOLASIB | Time drift report not received
4 | MANIPUR | TIPAIMUKH | Time drift report not received
5 | MEGHALAYA | KILLING | Time drift report not received
6 | NAGALAND | SANIS | Time drift report not received
7 | NAGALAND | KOHIMA | Time drift report not received
8 | TRIPURA | UDAIPUR | Time drift report not received
9 | NEEPCO | DOYANG | Time drift report not received
10 | NEEPCO | AGBPS | Time drift report not received
11 | NEEPCO | PANYOR LOWER | Time drift report not received
12 | NTPC | BGTPP | Time drift report not received
13 | POWERGRID | DIMAPUR | Time drift report not received
14 | POWERGRID | ROING | Time drift report not received
15 | POWERGRID | MARIANI | Time drift report not received
16 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | KARONG | Received on 21-05-2024

## 20 MAY 24-26 MAY 2024
Interconnection Metering Error Report for North-Eastern Region
Date of Reporting |  | 2024-05-30 | Year: | 2024-2025
| Period: | 2024-05-20 | To: | 2024-05-26
|  | Total number of Interface Meters | 547
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 50%). From 24-05-2024 value is zero | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT connectivity checking required
5 | ASSAM | MARIANI | AS-03 | 220 kV MARIANI(AS) END OF KATHALGURI FDR | NP-6888-A | Reads 33% less | 17:00 Hrs of 23/05/24 | 23:30 Hrs of 25/05/24 | - | Other end meter used for injection computation; CT/CVT connectivity checking required
6 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 19:00 Hrs of 26/05/24 | Till end of the week | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | NANGALBIBRA |  | 132kV AGIA-NANGALBIBRA | NP-9945-A | Main Meter | Weekly Drift correction required
8 | NEEPCO | PARE |  | PARE GT 1 of Unit 1 | NP-9554-A | Standby Meter | Weekly Drift correction required
8 | NEEPCO | AgGBPS |  | 132KV AgGBPS END OF AGARTALA FDR 1 | NP-9081-A | Main Meter | Weekly Drift correction required
9 | NEEPCO | AgGBPS |  | 132KV AgGBPS END OF AGARTALA FDR 1 | NP-9513-A | Check Meter | Weekly Drift correction required
10 | NEEPCO | AgGBPS |  | 132KV AgGBPS END OF AGARTALA FDR 2 | NP-9093-A | Main Meter | Weekly Drift correction required
11 | NEEPCO | AgGBPS |  | GTG # 2 | NP-9605-A | Standby Meter | Weekly Drift correction required
12 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
13 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
13 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
14 | NEEPCO | KOPILI |  | HV SIDE OF GT OF UNIT 4 | NE-0123-A | Standby Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
16 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
17 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
18 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | ICT 2 HV SIDE | NE-0045-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 KV DIMPAUR(PG) END OF DIMAPUR FDR 2 | NP-9649-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | ARUNACHAL | TENGA | Time drift report not received
2 | MIZORAM | LUNGMUAL | Time drift report not received
3 | MIZORAM | KOLASIB | Time drift report not received
4 | MANIPUR | TIPAIMUKH | Time drift report not received
5 | MEGHALAYA | KILLING | Time drift report not received
6 | NAGALAND | SANIS | Time drift report not received
7 | NAGALAND | KOHIMA | Time drift report not received
8 | TRIPURA | UDAIPUR | Time drift report not received
9 | NEEPCO | DOYANG | Time drift report not received
10 | NEEPCO | AGBPS | Time drift report not received
12 | NTPC | BGTPP | Time drift report not received
13 | POWERGRID | AIZAWL | Time drift report not received
13 | POWERGRID | IMPHAL | Time drift report not received
14 | POWERGRID | ROING | Time drift report not received
15 | POWERGRID | MARIANI | Time drift report not received
16 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
3 | POWERGRID | BONGAIGAON | Received on 29-05-2024
4 | MIZORAM | KOLASIB | Received on 29-05-2024

## 27 MAY 24-02 JUNE 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 50%). From 24-05-2024 value is zero | 2024-04-01 | 16:15 Hrs of 27-05-2024 | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
6 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 15:00 Hrs of 27-05-24 | 16:30 Hrs of 28-05-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | NANGALBIBRA |  | 132kV AGIA-NANGALBIBRA | NP-9945-A | Main Meter | Weekly Drift correction required
7 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
8 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA II | NP-5291-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 400 kV MISA END OF SILCHAR I | NP-9928-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | ARUNACHAL | TENGA | Time drift report not received
2 | MIZORAM | LUNGMUAL | Time drift report not received
3 | MIZORAM | KOLASIB | Time drift report not received
4 | NAGALAND | SANIS | Time drift report not received
5 | NAGALAND | KOHIMA | Time drift report not received
6 | TRIPURA | UDAIPUR | Time drift report not received
7 | NEEPCO | DOYANG | Time drift report not received
8 | NEEPCO | AGBPP | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | POWERGRID | ROING | Time drift report not received
12 | POWERGRID | MARIANI | Time drift report not received
13 | POWERGRID | SILCHAR | Time drift report not received
14 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | TRIPURA | UDAIPUR | Received on 05-06-2024
3 | MEGHALAYA | NANGALBIBRA | Received on 05-06-2024
4 | ASSAM | GOHPUR | Received on 05-06-2024
5 | MANIPUR | TIPAIMUKH | Received on 05-06-2024

## 03 JUNE 24-09 JUNE 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 50%). From 24-05-2024 value is zero | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 00:00 Hrs of 03-06-24 | 12:00 Hrs of 03-06-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | NANGALBIBRA |  | 132kV AGIA-NANGALBIBRA | NP-9945-A | Main Meter | Weekly Drift correction required
7 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
8 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | MISA |  | 400 kV MISA END OF KOPILI 3 | NE-0063-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | 400 kV MISA END OF SILCHAR I | NP-9928-A | Standby Meter | Weekly Drift correction required
17 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
19 | ASSAM | AZARA |  | 400KV AZARA END OF SILCHAR | NP-9981-A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
21 | POWERGRID | KHLEIHRIAT |  | KHLRT(PG) END OF BADARPUR(PG) FDR | NP-8477-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NTPC | BGTPP | Time drift report not received
8 | POWERGRID | ROING | Time drift report not received
9 | ARUNACHAL PRADESH | TENGA | Time drift report not received
10 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
3 | MIZORAM | LUANGMUAL | Received on 12-06-2024

## 10 JUNE 24-16 JUNE 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 50%). | 2024-04-01 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 23:30 Hrs of 12-06-24 | 16:15 Hrs of 13-06-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
6 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 21:00 Hrs of 14-06-24 | 12:00 Hrs of 15-06-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
7 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 23:15 Hrs of 15-06-24 | 13:15 Hrs of 16-06-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NP-6148-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | BTPS |  | 220 kV BTPS END OF SALAKATI FDR-2 | NP-9070-A | Main Meter | Weekly Drift correction required
3 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AZARA |  | 400KV AZARA END OF SILCHAR | NP-9981-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
8 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | NANGALBIBRA |  | 132kV AGIA-NANGALBIBRA | NP-9945-A | Main Meter | Weekly Drift correction required
10 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220/132 kV ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | HAFLONG |  | 132kV HAFLONG(PG) END OF UMRANGSHO FDR | NP-8502-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MISA |  | 400 kV MISA END OF KOPILI 3 | NE-0063-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MISA |  | 400 kV MISA END OF SILCHAR I | NP-9928-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
23 | POWERGRID | KHLEIHRIAT |  | KHLRT(PG) END OF BADARPUR(PG) FDR | NP-8477-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | ARUNACHAL PRADESH | TENGA | Time drift report not received
11 | POWERGRID | AIZAWL | Time drift report not received
12 | POWERGRID | SILCHAR | Time drift report not received
13 | POWERGRID | MISA | Time drift report not received
14 | POWERGRID | MARIANI | Time drift report not received
15 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | YUREMBAM | Received on 20-06-2024
4 | ASSAM | SARUSAJAI | Received on 19-06-2024
5 | POWERGRID | RANGIA | Received on 19-06-2024
6 | MIZORAM | KOLASIB | Received on 19-06-2024

## 17 JUNE 24-23 JUNE 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 2024-04-01 | 18:00 Hrs of 19-06-2024 | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 2024-06-17 | 12:45 Hrs of 19-06-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
6 | MEGHALAYA | KILLING | ME-15 | BYRNIHAT END OF 400 KV BONGAIGAON | NP-8370-A | Erratic Reading | 2024-06-17 | 05:45 Hrs of 20-06-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
7 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NE-0103-A | Reads 33% more | 2024-06-17 | Till end of the week | SANIS | CT/CVT ratio used for metering may be re-confirmed.
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NE-0103-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 kV PAVOI END OF BNC-2 FEEDER | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | ASSAM | AZARA |  | 400KV AZARA END OF SILCHAR | NP-9981-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-II | NP-9509-A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220/132 kV ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(NA) 2 | NP-9649-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MISA |  | 400 kV MISA END OF BALIPARA 2 | NP-5291-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | PANYOR | Time drift report not received
8 | NEEPCO | DHEP | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | BONGAIGAON | Time drift report not received
11 | ARUNACHAL PRADESH | TENGA | Time drift report not received
15 | POWERGRID | MARIANI | Time drift report not received
16 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | POWERGRID | RANGIA | Received on 26-06-2024
4 | MIZORAM | KOLASIB | Received on 26-06-2024

## 24 JUNE 24-30 JUNE 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MIZORAM | SHHIMUI | MZ-17 | 132 kV SHIMUI END OF MELRIAT(PG)-II | NP-9493-A | Reads 66 % less | 2024-06-26 | Till end of the week | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
6 | MIZORAM | SHHIMUI | MZ-18 | 132 kV SHIMUI END OF MELRIAT(PG)-I | NP-9496-A | Reads 66 % less | 2024-06-26 | Till end of the week | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
7 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 18:00 Hrs of 28-06-2024 | Till end of the week | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NE-0103-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 07 mins 13 secs
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220 kV SONABIL-BALIPARA II FDR | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | ASSAM | AZARA |  | 400KV AZARA END OF SILCHAR | NP-9981-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132 kV ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(NA) 2 | NP-9649-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(NA) 1 | NP-9602-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF IMPHAL | NP-9598-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 220/132 kV ICT 1 HV | NE-0032-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BALIPARA |  | 400 kV BALIPARA END OF MISA 2 | NP-5285-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 400 kV BALIPARA END OF BNC 4 | NP-9484-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 220 kV BALIPARA END OF SONABIL | NP-9487-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | BALIPARA |  | 132 kV BALIPARA END OF KHUPI | NP-9606-A | Main Meter | Weekly Drift correction required
25 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
26 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | BONGAIGAON |  | 220 kV BONGAIGAON END OF SALAKATI FDR-02 | NP-5780-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MISA |  | ICT# 3 400 KV SIDE | NP-9401-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
32 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | NEEPCO | AGBPP | Time drift report not received
5 | NEEPCO | DHEP | Time drift report not received
6 | NTPC | BGTPP | Time drift report not received
7 | POWERGRID | ROING | Time drift report not received
8 | POWERGRID | SILCHAR | Time drift report not received
9 | ARUNACHAL PRADESH | TENGA | Time drift report not received
10 | POWERGRID | MARIANI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | ASSAM | KAHELIPARA | Not Received. Laptop issue stated
4 | MIZORAM | LUANGMUAL | Not Received. Format not supported
5 | NAGALAND | KOHIMA | Received on 03-07-2024
6 | NAGALAND | SANIS | Received on 03-07-2024
7 | MANIPUR | YUREMBAM | Received on 03-07-2024

## 01 JULY 24-07 JULY 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). Reaing zero from 08:45 hrs of 02-07-24 | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MIZORAM | SHHIMUI | MZ-17 | 132 kV SHIMUI END OF MELRIAT(PG)-II | NP-9493-A | Reads 66 % less | 2024-06-26 | Till end of the week | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
6 | MIZORAM | SHHIMUI | MZ-18 | 132 kV SHIMUI END OF MELRIAT(PG)-I | NP-9496-A | Reads 66 % less | 2024-06-26 | Till end of the week | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
7 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 18:00 Hrs of 28-06-2024 | 09:45 hrs of 02-07-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
8 | MEGHALAYA | KILLING | ME-15 | 400 kV KILLING END OF SILCHAR FDR | NP-8371-A | Erratic Reading | 19:00 Hrs of 04-07-2024 | 00:00 hrs of 06-07-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NE-0103-A | High time drift | 2023-08-14 | Till end of the week | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 07 mins 13 secs
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | ASSAM | AZARA |  | 400KV AZARA END OF SILCHAR | NP-9981-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132 kV ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(NA) 2 | NP-9649-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF IMPHAL | NP-9598-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 400 kV BALIPARA END OF BNC 4 | NP-9484-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
26 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MISA |  | ICT# 3 400 KV SIDE | NP-9401-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
31 | POWERGRID | SM NAGAR |  | 132kV S.M.Nagar-Comilla I | NP-9078-A | Main Meter | Weekly Drift correction required (same issue stated in two consecutive weeks)
32 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | POWERGRID | SILCHAR | Time drift report not received
12 | ARUNACHAL PRADESH | TENGA | Time drift report not received
13 | POWERGRID | SALAKATI | Time drift report not received
14 | POWERGRID | MARIANI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | ASSAM | KAHELIPARA | Not Received. Laptop issue stated
4 | MIZORAM | LUANGMUAL | Received on 10-07-2024
5 | POWERGRID | BALIPARA | Received on 10-07-2024
6 | POWERGRID | RANGIA | Received on 10-07-2024
7 | POWERGRID | DIMAPUR | Received on 10-07-2024. Issue with DCD cable.

## 08 JULY 24-14 JULY 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). Reaing zero from 08:45 hrs of 02-07-24 to 11:45 hrs of 09-07-24 | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MIZORAM | SHHIMUI | MZ-17 | 132 kV SHIMUI END OF MELRIAT(PG)-II | NP-9493-A | Reads 66 % less | 2024-06-26 | Till end of the week | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
6 | MIZORAM | SHHIMUI | MZ-18 | 132 kV SHIMUI END OF MELRIAT(PG)-I | NP-9496-A | Reads 66 % less | 2024-06-26 | Till end of the week | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | NAGALAND | SANIS | NG-22 | 132 kV SANIS END OF DOYANG FDR | NE-0103-A | High time drift | 2023-08-14 | 2024-08-11 | SANIS | Other end meter used for drawal computation; time drift corrective action required
2 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
3 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 07 mins 13 secs
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | AZARA |  | 400KV AZARA END OF SILCHAR | NP-9981-A | Main Meter | Weekly Drift correction required
4 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR FDR | NP-9904-A | Main Meter | Weekly Drift correction required
5 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | NEEPCO | AgGBPS |  | STG # 2 GT | NP-9082-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220/132 kV ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(NA) 2 | NP-9649-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF IMPHAL | NP-9598-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MOKOKCHUNG |  | 132 kV MOKOKCHUNG PG END OF MOKOKCHUNG- 1 | NE-0012-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MOKOKCHUNG |  | 132 kV MOKOKCHUNG STATE END OF MOKOKCHUNG- 1 | NP-9653-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | MOKOKCHUNG |  | 132 kV MOKOKCHUNG STATE END OF MOKOKCHUNG- 2 | NP-9655-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | MOKOKCHUNG |  | 132 kV MOKOKCHUNG STATE END OF MARIANI- 1 | NE-0128-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 132 kV BALIPARA END OF KHUPI FDR | NP-9606-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 220 kV MISA END OF DIMAPUR #2 | NE-0023-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
28 | POWERGRID | BNC |  | 400 kV BNC - LOWER SUBANSIRI CKT 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | DIMAPUR | Time drift report not received
11 | POWERGRID | AIZAWL | Time drift report not received
12 | POWERGRID | SILCHAR | Time drift report not received
13 | ARUNACHAL PRADESH | TENGA | Time drift report not received
14 | POWERGRID | SALAKATI | Time drift report not received
15 | POWERGRID | BONGAIGAON | Time drift report not received
16 | POWERGRID | NIRJULI | Time drift report not received
17 | POWERGRID | MARIANI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated

## 15 JULY 24-21 JULY 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MIZORAM | SHHIMUI | MZ-17 | 132 kV SHIMUI END OF MELRIAT(PG)-II | NP-9493-A | Reads 66 % less | 2024-06-26 | 15-07-2024 (11:30 HRS) | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
6 | MIZORAM | SHHIMUI | MZ-18 | 132 kV SHIMUI END OF MELRIAT(PG)-I | NP-9496-A | Reads 66 % less | 2024-06-26 | 15-07-2024 (11:30 HRS) | SHHIMUI/MELRIAT | Other end meter used for injection computation; CT/PT connectivity checking required
7 | OTPCL | PALATANA | PL-02/ PL-17 | 400 kV PALATANA END OF SILCHAR II | NP-0010-A/ NP-9560-A | Erratic Reading (Around 30%) | 15-07-2024 (11:00 Hrs) | 15-07-2024 (11:30 Hrs) | - | Other end meter used for injection computation; CT connectivity checking required
8 | POWERGRID | BONGAIGAON | AS-25 | 400 KV BINAGURI(PG)-BONGAIGAON(NER)-1 | NE-0154-A | Erroneous reading | 19-07-2024 (10:45 Hrs) | 19-07-2024 (10:45 Hrs) | - | Other end meter used for injection computation; CT connectivity checking required
9 | POWERGRID | BONGAIGAON | AS-26 | 400 KV BINAGURI(PG)-BONGAIGAON(NER)-2 | NE-0104-A | Erroneous reading | 19-07-2024 (10:45 Hrs) | 19-07-2024 (10:45 Hrs) | - | Other end meter used for injection computation; CT connectivity checking required
10 | POWERGRID | BONGAIGAON | AS-97 | 400 KV ALIPURDUAR(PG)-BONGAIGAON(NER)-1 | NP-0106-A | Erroneous reading | 19-07-2024 (10:45 Hrs) | 19-07-2024 (10:45 Hrs) | - | Other end meter used for injection computation; CT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 07 mins
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | AGIA |  | 132kV AGIA END OF NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
3 | ASSAM | AGIA |  | 132kV AGIA END OF MENDIPATHAR | NP-9455-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
13 | POWERGRID | DIMAPUR |  | 220/132 kV ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR(NA) 2 | NP-9649-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF IMPHAL | NP-9598-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MOKOKCHUNG |  | 132 kV MOKOKCHUNG STATE END OF MOKOKCHUNG- 2 | NP-9655-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | BALIPARA |  | 132 kV BALIPARA END OF KHUPI FDR | NP-9606-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
20 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
22 | INDIGRID | SM NAGAR |  | Bay 101_SM NAGAR (TSECL LINE) | NP-9890-A | Main Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | MEGHALAYA | UMTRU | Time drift report not received
6 | TRIPURA | UDAIPUR | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | DHEP | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | POWERGRID | ROING | Time drift report not received
11 | POWERGRID | DIMAPUR | Time drift report not received
12 | POWERGRID | AIZAWL | Time drift report not received
13 | ARUNACHAL PRADESH | TENGA | Time drift report not received
14 | POWERGRID | BALIPARA | Time drift report not received
15 | POWERGRID | NIRJULI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | MEGHALAYA | UMTRU | Data Not Received For Meter No. NE-0016-A
4 | NEEPCO | KHANDONG | Data Not Received For Meter No.NE-0171-A & NE-0173-A

## 22 JULY 24-28 JULY 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 07 mins
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | TINSUKIA |  | 220 kV TINSUKIA END OF AGBPP II | NP-9658-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | HAILAKANDI |  | 132 kV SILCHAR 2 | NP-9478-A | Standby Meter | Weekly Drift correction required
5 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-II | NP-9509-A | Check Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF IMPHAL | NP-9598-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR 1 | NP-9602-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 2 | NE-0070-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 1 | NE-0109-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR 2 | NP-9649-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | ICT 3 LV | NP-6889-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | ICT 2 LV | NP-9448-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | DIMAPUR |  | ICT 1 HV | NE-0032-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | DIMAPUR |  | ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
25 | POWERGRID | BALIPARA |  | 400KV B.Chariali#3 AT Balipara | NP-9486-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
28 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | MISA |  | 220 kV Misa end of Samaguri # 2 | NP-9502-A | Main Meter | Weekly Drift correction required
31 | POWERGRID | MISA |  | 220 kV Misa end of Silchar #2 | NP-9929-A | Standby Meter | Weekly Drift correction required
32 | POWERGRID | MISA |  | 220 kV MISA END OF KOPILI #2 | NE-0062-A | Standby Meter | Weekly Drift correction required
33 | POWERGRID | SILCHAR |  | 400kV ICT 1 | NE-0050-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | ARUNACHAL PRADESH | TENGA | Time drift report not received
12 | POWERGRID | SALAKATI | Time drift report not received
13 | POWERGRID | NIRJULI | Time drift report not received
14 | POWERGRID | IMPHAL | Time drift report not received/same file sent every week
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | POWERGRID | HAFLONG | Received on 31-07-2024

## 29 JULY 24-04 AUGUST 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 07 mins
3 | POWERGRID | BALIPARA | ZZ-36 | 400KV B.Chariali#3 at Balipara | NP-9486-A | High time drift | 2024-08-05 | Till end of the week | BALIPARA | High Time Drift of 06 mins
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | TINSUKIA |  | 220 kV TINSUKIA END OF AGBPP II | NP-9658-A | Standby Meter | Weekly Drift correction required
4 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
5 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-II | NP-9509-A | Check Meter | Weekly Drift correction required
13 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR 1 | NP-9602-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 2 | NE-0070-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 1 | NE-0109-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR(PG) END OF DIMAPUR 2 | NP-9649-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | ICT 3 LV | NP-6889-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | ICT 1 HV | NE-0032-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MISA |  | 220 kV Misa end of Samaguri # 2 | NP-9502-A | Main Meter | Weekly Drift correction required
27 | POWERGRID | MISA |  | 220 kV Misa end of Silchar #2 | NP-9929-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | MISA |  | 220 kV MISA END OF KOPILI #2 | NE-0062-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | SILCHAR |  | 400kV ICT 1 | NE-0050-A | Standby Meter | Weekly Drift correction required
30 | INDIGRID | SM NAGAR |  | Bay 101_SM NAGAR (TSECL LINE) | NP-9890-A | Main Meter | Weekly Drift correction required
31 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Main Meter | Weekly Drift correction required
32 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
33 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | POWERGRID | SILCHAR | Time drift report not received
12 | POWERGRID | NIRJULI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated

## 05 AUGUST 24-11 AUGUST 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection possible
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection possible
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 05 mins
3 | POWERGRID | BALIPARA | ZZ-36 | 400KV B.Chariali#3 at Balipara | NP-9486-A | High time drift | 2024-08-05 | Till end of the week | BALIPARA | High Time Drift of 06 mins
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
5 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
7 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-II | NP-9509-A | Check Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 2 | NE-0070-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 1 | NE-0109-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | ICT 3 LV | NP-6889-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | DIMAPUR |  | ICT 1 HV | NE-0032-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | HAFLONG |  | Bay no. 102- Haflong - Umrangsho | NP-8502-A | Main Meter | Weekly Drift correction required
23 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
24 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MISA |  | BALIPARA #1 | NP-5299-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MISA |  | 220 kV KOPILI #1 | NE-0061-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | BNC |  | 400 Kv BNC- RGN Ckt-II | NP-9086-A | Standby Meter | Weekly Drift correction required
31 | POWERGRID | BNC |  | 132 Kv BNC- PAVOI Ckt-I (BNC end) | NP-9678-A | Standby Meter | Weekly Drift correction required
32 | POWERGRID | BNC |  | POLE II | NP-5798-A | Main Meter | Weekly Drift correction required
32 | POWERGRID | SILCHAR |  | 400 kV Imphal II | NE-0040-A | Standby Meter | Weekly Drift correction required
33 | INDIGRID | SM NAGAR |  | Bay 101_SM NAGAR (TSECL LINE) | NP-9890-A | Main Meter | Weekly Drift correction required
34 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
34 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | POWERGRID | NIRJULI | Time drift report not received
12 | POWERGRID | BALIPARA | Time drift report not received
13 | POWERGRID | IMPHAL | Time drift report not received/same file sent every week
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
4 | MANIPUR | RENGPANG | Not Received. Faulty DCD Cable stated
5 | NAGALAND | SANIS | Not Received. Mailed to concerened
6 | POWERGRID | BALIPARA | Received on 14-08-2024

## 12 AUGUST 24-18 AUGUST 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection possible
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection possible
7 | MEGHALAYA | KILLING | ME-15 | 400 kV BYRNIHAT END OF SILCHAR LINE | NP-8371-A | Erratic Reading | 00:00 Hrs of 12-06-2024 | 10:15 Hrs of 12-06-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity/tightness checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 03 mins
3 | POWERGRID | BALIPARA | ZZ-36 | 400KV B.Chariali#3 at Balipara | NP-9486-A | High time drift | 2024-08-05 | Till end of the week | BALIPARA | High Time Drift of 06 mins
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | CHIMPU |  | 132 kV Pare Ckt II | NP-9587 A | Standby Meter | Weekly Drift correction required
3 | ARUNACHAL PRADESH | CHIMPU |  | 132 kV BNC Ckt I | NP-9935 A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
6 | ASSAM | MIRZA |  | 400 kV MIRZA END OF BONGAIGAON FDR | NP-9983-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
8 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
12 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
13 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
14 | NEEPCO | AgGBPS |  | LINE # 1 (New Meter) | NP-9513-A | Check Meter | Weekly Drift correction required
15 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Main Meter | Weekly Drift correction required
16 | NEEPCO | AgGBPS |  | LINE # 3 (Old Meter) | NP-9080-A | Main Meter | Weekly Drift correction required
17 | NEEPCO | AgGBPS |  | LINE # 3 (New Meter) | NP-9515-A | Check Meter | Weekly Drift correction required
18 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
19 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
20 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
21 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
22 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9509A | Check Meter | Weekly Drift correction required
23 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-II | NP-9509-A | Check Meter | Weekly Drift correction required
24 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 2 | NE-0070-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | DIMAPUR |  | 220 kV DIMAPUR(PG) END OF MISA 1 | NE-0109-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
27 | POWERGRID | DIMAPUR |  | ICT 3 LV | NP-6889-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | DIMAPUR |  | ICT 1 HV | NE-0032-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | DIMAPUR |  | ICT 2 HV | NE-0045-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
31 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
32 | POWERGRID | HAFLONG |  | Bay no. 102- Haflong - Umrangsho | NP-8502-A | Main Meter | Weekly Drift correction required
33 | POWERGRID | NIRJULI |  | ICT-II HV SIDE | NP-9662 A | Main Meter | Weekly Drift correction required
34 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
35 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
36 | POWERGRID | MISA |  | DIMAPUR #2 | NE 0023 A | Standby Meter | Weekly Drift correction required
37 | POWERGRID | MISA |  | New Mariani #1 | NP 9892 A | Standby Meter | Weekly Drift correction required
38 | POWERGRID | BNC |  | 400 Kv BNC- RGN Ckt-II | NP-9086-A | Standby Meter | Weekly Drift correction required
39 | POWERGRID | BNC |  | 132 Kv BNC- PAVOI Ckt-I (BNC end) | NP-9678-A | Standby Meter | Weekly Drift correction required
40 | POWERGRID | BNC |  | POLE II | NP-5798-A | Main Meter | Weekly Drift correction required
41 | POWERGRID | MOKOKCHUNG |  | 220/132 kV ICT-1 (LV Side) | NP-9923-A | Standby Meter | Weekly Drift correction required
42 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
43 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
44 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | POWERGRID | NIRJULI | Time drift report not received
12 | POWERGRID | IMPHAL | Time drift report not received/same file sent every week
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
4 | MANIPUR | RENGPANG | Not Received. Faulty DCD Cable stated

## 19 AUGUST 24-25 AUGUST 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NE-0018-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | MEGHALAYA | KILLING | ME-15 | 400 kV BYRNIHAT END OF SILCHAR LINE | NP-8371-A | Erratic Reading | 00:00 Hrs of 19-08-2024 | 15:30 Hrs of 21-08-2024 | KILLING | Other end meter used for injection computation; CT/CVT connectivity/tightness checking required
8 | ASSAM | AZARA | AS-93 | 400 kV AZARA END OF SILCHAR LINE | AS-89 | Erratic Reading | 19:00 Hrs of 19-08-2024 | 09:45 Hrs of 21-08-2024 | - | Other end meter used for injection computation; CT/CVT connectivity/tightness checking required
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | High Time Drift of 03 mins
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | CHIMPU |  | 132 kV BNC Ckt I | NP-9935 A | Main Meter | Weekly Drift correction required
3 | ASSAM | DULLAVCHERRA |  | 132 kV Dullavcherra-Dharmanagar Feeder | NP-9904-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
6 | ASSAM | MIRZA |  | 400 kV MIRZA END OF BONGAIGAON FDR | NP-9983-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
8 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | LUMSHNONG |  | 132kV LUMSHNONG END OF PANCHGRAM | NP-8384-A | Main Meter | Weekly Drift correction required
10 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | DIMAPUR |  | ICT 3 LV | NP-6889-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BALIPARA |  | 400KV Kameng#1 | NP-9612-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 400/220 kV ICT#2 (LV) | NP-5800-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 400KV Misa#2 | NP-5285-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BALIPARA |  | 400KV B.Chariali#1 | NP-9485-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | HAFLONG |  | 132 kV Haflong(AEGCL) end of Haflong | NE-0026-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MISA |  | DIMAPUR #1 | NE 0006 A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MISA |  | Silchar #1 | NP 9928 A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | BNC |  | 400 Kv BNC- RGN Ckt-II | NP-9086-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | BNC |  | 132 Kv BNC- PAVOI Ckt-I (BNC end) | NP-9678-A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | BNC |  | POLE II | NP-5798-A | Main Meter | Weekly Drift correction required
31 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
32 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 3 | NE-0092-A | Standby Meter | Weekly Drift correction required
33 | POWERGRID | MOKOKCHUNG |  | 220 kV Mariani-Mokokchung- 1 | NE-0128-A | Standby Meter | Weekly Drift correction required
34 | POWERGRID | MOKOKCHUNG |  | 220/132 kV ICT-1 (LV Side) | NP-9923-A | Standby Meter | Weekly Drift correction required
35 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
36 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
37 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | NAGALAND | SANIS | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | POWERGRID | IMPHAL | Time drift report not received/same file sent every week
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | MANIPUR | RENGPANG | Not Received. Faulty DCD Cable stated
4 | POWERGRID | ZIRO | Received on 28-08-2024
5 | POWERGRID | RANGIA | Received on 28-08-2024
6 | POWERGRID | BALIPARA | Received on 28-08-2024
7 | TRIPURA | UDAIPUR | Received on 28-08-2024

## 26 AUGUST 24-01 SEPT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | SALAKATI | AS-33 | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | High time drift | 2024-06-26 | Till end of the week | SALAKATI | Time Drift of 02 mins 11 sec
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | DULLAVCHERRA |  | 132 kV Dullavcherra-Dharmanagar Feeder | NP-9904-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
5 | INDIGRID | SM NAGAR |  | TERTIARY (Common for Bank 1&2) | NP-9969-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | UNIT 2 GT | NP-9047-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-I | NP-9065-A | Main Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
14 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
15 | POWERGRID | DIMAPUR |  | ICT 3 LV | NP-6889-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) SIDE | NP-6151-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BALIPARA |  | 400/220 kV ICT#2 (LV) | NP-5800-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BALIPARA |  | 400KV B.Chariali#1 | NP-9485-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | Samaguri # 1 | NE 0006 A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NP 9928 A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MOKOKCHUNG |  | 132 kV Mokokchung-Mokokchung- 2 | NE-0021-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
10 | POWERGRID | AIZAWL | Time drift report not received
11 | POWERGRID | IMPHAL | Time drift report not received/same file sent every week
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | MANIPUR | RENGPANG | Not Received. Faulty DCD Cable stated
4 | MIZORAM | LUNGMUAL | Received on 04-09-2024

## 02 SEPT 24-08 SEPT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | BHUTAN | MOTANGA | ER-08 | 132 kV MOTANGA END OF RANGIA | ER-2049-A | Read zero | 13:45 Hrs of 08-09-24 | 13:45 Hrs of 08-09-24 | - | CT/CVT connectivity checking required.
8 | NEEPCO | PANYOR | RN-18 | 132 kV PANYOR END OF PARE T/L | NP-9439-A | Erratic Reading (Around 66%). | 13:45 Hrs of 02-09-24 | 14:30 Hrs of 02-09-24 | - | CT/CVT connectivity issue. Phase disconnection likely. Other end meter used for injection computation
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | DULLAVCHERRA |  | 132 kV Dullavcherra-Dharmanagar Feeder | NP-9904-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
5 | INDIGRID | PK BARI |  | Bay 102- Ambasa (TSECL) | NP-9930-A | Main Meter | Weekly Drift correction required
6 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF NIRJULI FDR | NE-0119-A | Main Meter | Weekly Drift correction required
7 | STERLITE | NORTH LAKHIMPUR |  | 132KV NORTH LAKHIMPUR END OF PARE FDR | NE-0117-A | Main Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
13 | KMTL | NEW KOHIMA |  | 400/220 kV ICT-2 HV (Bay-410) | NP-9987-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | ROING |  | 132 kV CHAPAKHOWA END OF ROING 2 | NE-0060-A | Main Meter | Weekly Drift correction required
15 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 1 | NE-0059-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 2 | NE-0056-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | Srikona 1 | NP-9895-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | SILCHAR |  | 400kV ICT 2 | NE-0049-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | SILCHAR |  | Pallatana 2 | NE-0042-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | SILCHAR |  | Pallatana 1 | NE-0030-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | SILCHAR |  | Imphal 2 | NE-0040-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | SALAKATI |  | 220 kV SALAKATI END OF ALIPURDUAR 1 | NP-7581-A | Main Meter | Weekly Drift correction required
23 | POWERGRID | DIMAPUR |  | 132 kV DIMAPUR END OF KOHIMA | NP-8472-A | Main Meter | Weekly Drift correction required
24 | POWERGRID | DIMAPUR |  | ICT 3 LV | NP-6889-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
26 | POWERGRID | BALIPARA |  | 400/220 kV ICT#2 (LV) | NP-5800-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | BALIPARA |  | 400KV B.Chariali#1 | NP-9485-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | IMPHAL PG |  | 132kV IMPHAL-IMPHAL 1 | NP-8378-A | Standby Meter | Weekly Drift correction required
29 | POWERGRID | MISA |  | Samaguri # 1 | NE 0006 A | Standby Meter | Weekly Drift correction required
30 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NP 9928 A | Standby Meter | Weekly Drift correction required
31 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
32 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 3 | NE-0092-A | Standby Meter | Weekly Drift correction required
33 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
34 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | MISA | Time drift report not received
10 | POWERGRID | IMPHAL | Time drift report not received/same file sent every week
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | MANIPUR | RENGPANG | Not Received. Faulty DCD Cable stated
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | STERLITE | HATSINGIMARI | Not Received. Mailed to concerened
6 | STERLITE | AMPATI | Not Received. Mailed to concerened
7 | ASSAM | SAMAGURI | Received on 11-09-2024
8 | POWERGRID | ZIRO | Received on 11-09-2024
9 | POWERGRID | IMPHAL | Received on 11-09-2024

## 09 SEPT 24-15 SEPT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | STERLITE | AMPATI | ME-18 | 132 kV AMPATI END OF HATSINGIMARI 1 | NE-0074-A | Erratic Reading | 00:00 Hrs of 09-09-2024 | 17:00 Hrs of 09-09-2024 | - | CT/CVT connectivity issue. Phase disconnection likely. Other end meter used for injection computation
8 | STERLITE | AMPATI | ME-19 | 132 kV AMPATI END OF HATSINGIMARI 2 | NE-0157-A | Erratic Reading | 00:00 Hrs of 09-09-2024 | 17:30 Hrs of 09-09-2024 | - | CT/CVT connectivity issue. Phase disconnection likely. Other end meter used for injection computation
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till end of the week | IMPHAL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | INDIGRID | SMNAGAR |  | Bay 404_P K BARI Ckt-01 | NP-9978-A | Standby Meter | Weekly Drift correction required
5 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
8 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
10 | POWERGRID | ROING |  | 132 kV CHAPAKHOWA END OF ROING 2 | NE-0060-A | Main Meter | Weekly Drift correction required
11 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 1 | NE-0059-A | Main Meter | Weekly Drift correction required
12 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 2 | NE-0056-A | Main Meter | Weekly Drift correction required
13 | POWERGRID | DIMAPUR |  | 132 kV BOKAJAN END OF DIMAPUR(PG) | NP-7587-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400/220 kV ICT#2 (LV) | NP-5800-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BALIPARA |  | 400KV B.Chariali#1 | NP-9485-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | ICT#2 220 KV SIDE | NE 0008 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 3 | NE-0092-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
21 | NEEPCO | PARE |  | 132KV PARE-NORTH LAKHIMPUR | NP 9542 A | Check Meter | Weekly Drift correction required
22 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
23 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
24 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NEEPCO | PANYOR LOWER | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | STERLITE | HATSINGIMARI | Time drift report not received
11 | STERLITE | AMPATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Faulty DCD Charger stated
3 | MANIPUR | RENGPANG | Not Received. Faulty DCD Cable stated
4 | ASSAM | TINSUKIA | Laptop with Softwae damaged.
5 | MIZORAM | KOLASIB | Received on 19-09-2024
6 | MANIPUR | YUREMBAM | Received on 19-09-2024
7 | MANIPUR | THOUBAL | Received on 19-09-2024
8 | POWERGRID | MISA | Received on 18-09-2024
9 | POWERGRID | MARIANI | Received on 18-09-2024
10 | ASSAM | SARUSAJAI | Received on 18-09-2024
11 | ASSAM | MARIANI | Received on 18-09-2024

## 16 SEPT 24-22 SEPT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till end of the week | IMPHAL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | POWERGRID | BADARPUR |  | 132kV Badarpur-Silchar-2 T/L | NP-8495-A | Standby Meter | Weekly Drift correction required
2 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
6 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | POWERGRID | ROING |  | 132 kV CHAPAKHOWA END OF ROING 2 | NE-0060-A | Main Meter | Weekly Drift correction required
12 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 1 | NE-0059-A | Main Meter | Weekly Drift correction required
13 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 2 | NE-0056-A | Main Meter | Weekly Drift correction required
| POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) | NP-6151 | Standby Meter | Weekly Drift correction required
| POWERGRID | BALIPARA |  | 400KV Misa#1 | NE-0036 | Standby Meter | Weekly Drift correction required
| POWERGRID | BALIPARA |  | 400KV Misa#2 | NP-5285 | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BALIPARA |  | 400/220 kV ICT#2 (LV) | NP-5800-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BALIPARA |  | 400KV B.Chariali#1 | NP-9485-A | Standby Meter | Weekly Drift correction required
| POWERGRID | BALIPARA |  | 400KV BONG#2 | NE-0047-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | ICT#2 220 KV SIDE | NE 0008 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
| POWERGRID | MOKOKCHUNG |  | 132 kV Mokokchung-Mokokchung- 2 | NE-0021-A | Standby Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NEEPCO | PANYOR LOWER | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | POWERGRID | ROING | Time drift report not received
11 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | MANIPUR | RENGPANG | Not Received. Mailed to concerened
4 | ARUNACHAL PRADESH | TENGA | Data received of incompatible format. Mailed to concerened
5 | POWERGRID | ZIRO | Received on 25-09-2024
6 | ASSAM | MARIANI | Received on 25-09-2024
7 | NAGALAND | KOHIMA | Received on 25-09-2024
8 | MEGHALAYA | LUMSHNONG | Received on 25-09-2024

## 23 SEPT 24-29 SEPT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AS-54 | 220/132 KV ICT-1(LV) | NP-6891-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | 2024-09-23 | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till end of the week | IMPHAL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
8 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | INDIGRID | SM NAGAR |  | Bay 103_ICT Bank -1_IV | NP-9966-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | ROING |  | 132 kV CHAPAKHOWA END OF ROING 2 | NE-0060-A | Main Meter | Weekly Drift correction required
13 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 1 | NE-0059-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | CHAPAKHOWA |  | 132 kV ROING END OF CHAPAKHOWA 2 | NE-0056-A | Main Meter | Weekly Drift correction required
15 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) | NP-6151 | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | ICT#1 400 KV SIDE | NP 5300 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | ICT#1 220 KV SIDE | NE 0004 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MISA |  | BALIPARA #1 | NP 5299 A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MOKOKCHUNG |  | 132 kV Mokokchung-Mokokchung- 1 | NE-0012-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MOKOKCHUNG |  | 132 kV Doyang-Mokokchung TL | NP-9671-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | AIZAWL |  | 132 kV Aizawl-Kumarghat | NP-9707-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | AIZAWL |  | 132 kV Aizawl-Kolasib | NP-9610-A | Standby Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
27 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | ROING | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | MANIPUR | RENGPANG | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Received on 03-10-2024
5 | ASSAM | SARUSAJAI | Received on 03-10-2024
6 | MIZORAM | KOLASIB | Received on 02-10-2024
7 | MANIPUR | THOUBAL | Received on 02-10-2024
8 | NEEPCO | DOYANG | Received on 02-10-2024

## 30 SEPT 24-06 OCT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till end of the week | IMPHAL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
3 | NAGALAND | SANIS |  | 132 kV Doyang-Sanis | NE-0103-A | Standby Meter | Weekly Drift correction required
4 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
5 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
8 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
9 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
10 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
11 | INDIGRID | PK BARI |  | Bay-105-ICT-2 | NP-9908-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | BADARPUR |  | 132kV Badarpur-Badarpur(AEGCL) T/L | NP-6871-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | BADARPUR |  | 132kV Badarpur(AEGCL)-Badarpur T/L | NP-6872-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | Silchar #1 | NP 9928 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | Silchar #2 | NP 9929 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MISA |  | BALIPARA #1 | NP 5299 A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
21 | ASSAM | HAILAKANDI |  | 132 kV Silchar 1 | NP-5301-A | Mian Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
27 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
28 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
29 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
30 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
31 | NEEPCO | AgGBPS |  | LINE # 1 (New Meter) | NP-9513-A | Check Meter | Weekly Drift correction required
32 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Main Meter | Weekly Drift correction required
33 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Check Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | LINE # 3 (Old Meter) | NP-9080-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | TRIPURA | UDAIPUR | Time drift report not received
5 | NEEPCO | PANYOR | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
3 | MANIPUR | RENGPANG | Not Received. Mailed to concerened
4 | NAGALAND | KOHIMA | Received on 09-10-2024
5 | NAGALAND | SANIS | Received on 09-10-2024
6 | POWERGRID | KUMARGHAT | Received on 09-10-2024

## 07 OCT 24-13 OCT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG | NP-9947-A | Erratic Reading (Close to 0). | 16:15 Hrs of 09-10-2024 | Till end of the week | KOHIMA | CT/CVT connectivity checking required. Phase disconnection likely.Other end meter used for drawal computation
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till end of the week | IMPHAL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | SAMAGURI |  | 132 Kv SAMAGURI END OF MISA FDR II | NP-9713-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAILAPOOL |  | 132 Kv PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | Standby Meter | Weekly Drift correction required
7 | NAGALAND | SANIS |  | 132 kV Doyang-Sanis | NE-0103-A | Standby Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
12 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
15 | INDIGRID | PK BARI |  | Bay 103- ICT-1 | NP-9906-A | Standby Meter | Weekly Drift correction required
16 | INDIGRID | PK BARI |  | Bay 412- ICT-2 | NP-9907-A | Standby Meter | Weekly Drift correction required
17 | INDIGRID | PK BARI |  | Tertiary | NP-9909-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | BADARPUR |  | 132kV Badarpur(AEGCL)-Badarpur T/L | NP-6872-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | MISA |  | ICT#1 400 KV SIDE | NP 5300 A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MISA |  | Silchar #2 | NP 9929 A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | BALIPARA #1 | NP 5299 A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
24 | ASSAM | HAILAKANDI |  | 132 kV Silchar 1 | NP-5301-A | Mian Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
26 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | AgGBPS |  | STG # 1 | NP-9079-A | Standby Meter | Weekly Drift correction required
28 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
29 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
30 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
31 | NEEPCO | AgGBPS |  | LINE # 1 (New Meter) | NP-9513-A | Check Meter | Weekly Drift correction required
32 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Main Meter | Weekly Drift correction required
33 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Check Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | LINE # 3 (Old Meter) | NP-9080-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1) | NP-9940-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2) | NP-9941-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | TRIPURA | UDAIPUR | Time drift report not received
5 | NAGALAND | KOHIMA | Time drift report not received
6 | NAGALAND | SANIS | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | DHEP | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | POWERGRID | SALAKATI | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | RENGPANG | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Received on 17-10-2024
4 | MANIPUR | KARONG | Received on 16-10-2024
5 | POWERGRID | RANGIA | Received on 16-10-2024

## 14 OCT 24-20 OCT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
Sl. N. | Utility Name | Location /Substation | Location Code | Name of the feeder | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | NAGALAND | KOHIMA | NG-02 | 132 kV KOHIMA END OF KARONG | NP-9947-A | Erratic Reading (Close to 0). | 16:15 Hrs of 09-10-2024 | 17:30 Hrs of 16-10-2024 | KOHIMA | CT/CVT connectivity checking required. Phase disconnection likely.Other end meter used for drawal computation
B. Meter error due to any other reason
Sl. N. | Utility Name | Location /Substation | Location Code |  | Meter Number | Error in Meter | Duration from | Duration to | Corrective Action required from | Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till end of the week | IMPHAL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
Sl. No. | Utility Name | Location /Substation |  | Name of the feeder | Meter Number | Category | Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAILAPOOL |  | 132 Kv PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | Standby Meter | Weekly Drift correction required
7 | NAGALAND | SANIS |  | 132 kV SANIS END OF DOYANG | NE-0103-A | Standby Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
12 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF JIRIBAM-II | NP-9511-A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | UNIT # 2 | NP-9047-A | Standby Meter | Weekly Drift correction required
15 | INDIGRID | PK BARI |  | Bay 409- ICT-1 | NP-9905-A | Standby Meter | Weekly Drift correction required
16 | INDIGRID | PK BARI |  | Bay 103- ICT-1 | NP-9906-A | Standby Meter | Weekly Drift correction required
16 | INDIGRID | PK BARI |  | Bay-105-ICT-2 | NP-9908-A | Standby Meter | Weekly Drift correction required
17 | INDIGRID | PK BARI |  | Tertiary | NP-9909-A | Main Meter | Weekly Drift correction required
18 | POWERGRID | BADARPUR |  | 132kV Panchgram -Lumsnong T/L | NP-7595-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | MISA |  | ICT#1 400 KV SIDE | NP 5300 A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MISA |  | Silchar #2 | NP 9929 A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MISA |  | BALIPARA #1 | NP 5299 A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
26 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | AgGBPS |  | STG # 1 | NP-9079-A | Standby Meter | Weekly Drift correction required
28 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
29 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
30 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
31 | NEEPCO | AgGBPS |  | LINE # 1 (New Meter) | NP-9513-A | Check Meter | Weekly Drift correction required
32 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Main Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | LINE # 3 (Old Meter) | NP-9080-A | Main Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | LINE # 3 (New Meter) | NP-9515-A | Check Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2) | NP-9941-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
Sl. No. | Utility Name | Location /Substation | Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | TRIPURA | UDAIPUR | Time drift report not received
5 | ARUNACHAL | TENGA | Time drift report not received
6 | NAGALAND | KOHIMA | Time drift report not received
7 | NAGALAND | SANIS | Time drift report not received
8 | NEEPCO | AGBPP | Time drift report not received
9 | NEEPCO | DHEP | Time drift report not received
10 | NTPC | BGTPP | Time drift report not received
11 | MEGHALAYA | KHLEIHRIAT_ME | Time drift report not received
12 | POWERGRID | MISA | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
Sl. No. | Utility Name | Location /Substation | Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | NAGALAND | SANIS | Received on 24-10-2024
3 | MANIPUR | THOUBAL | Received on 23-10-2024
4 | MEGHALAYA | LUMSHNONG | Received on 23-10-2024 (LNT Software issue)
5 | TRIPURA | UDAIPUR | Received on 23-10-2024
6 | POWERGRID | RANGIA | Received on 23-10-2024

## 21 OCT 24-27 OCT 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF 400KV KAMENG-1 FDR | NP-9612-A | Erroneous reading (close to 0) | 21:00 Hrs of 24-10-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till end of the week | IMPHAL | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DULLAVCHERA FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | NAGALAND | SANIS |  | 132 kV SANIS END OF DOYANG | NE-0103-A | Standby Meter | Weekly Drift correction required
7 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
13 | POWERGRID | BADARPUR |  | 132kV Panchgram -Lumsnong T/L | NP-7595-A | Main Meter | Weekly Drift correction required
14 | POWERGRID | MISA |  | Silchar #1 | NP 9928 A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MARIANI_PG |  | 202- ICT#2 220 kV Side | NP-9959-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MARIANI_PG |  | 205- 220kV AEGCL Feeder | NE-0029-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | MARIANI_PG |  | 206- 220kV Kathalguri (NEEPCo) | NE-0034-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | MARIANI_PG |  | 207- 220kV Mokokchung #1 | NE-0046-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | MARIANI_PG |  | 208- 220kV Mokokchung #2 | NP-9911-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | MARIANI_PG |  | 211- Future#1 | NP-9914-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MARIANI_PG |  | 212- Future#2 | NP-9913-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MARIANI_PG |  | 406- 400kV ICT#1 400kV Side | NP-9951-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI_PG |  | 407- 400kV Misa#1 | NP-9952-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MARIANI_PG |  | 409- 400kV ICT#1 400kV Side | NP-9950-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MARIANI_PG |  | 410- 400kV Kohima#1 | NP-9974-A | Standby Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | TRIPURA | UDAIPUR | Time drift report not received
5 | ARUNACHAL | TENGA | Time drift report not received
6 | NAGALAND | KOHIMA | Time drift report not received
7 | NAGALAND | SANIS | Time drift report not received
8 | NEEPCO | AGBPP | Time drift report not received
9 | NEEPCO | DHEP | Time drift report not received
10 | NTPC | BGTPP | Time drift report not received
11 | POWERGRID | SALAKATI | Time drift report not received
12 | POWERGRID | DIMAPUR | Time drift report not received
13 | POWERGRID | ROING | Time drift report not received
14 | MEGHALAYA | KILLING | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Received on 30-10-2024
3 | MANIPUR | TIPAIMUKH | Received on 30-10-2024
4 | ASSAM | BTPS | Received on 30-10-2025
5 | POWERGRID | KUMARGHAT | Received on 30-10-2027

## 28 OCT 24-03 NOV 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | AM-38 | 400 kV BALIPARA END OF 400KV KAMENG-1 FDR | NP-9612-A | Erroneous reading (close to 0) | 21:00 Hrs of 24-10-2024 | Till 12:15 Hrs of 02-11-2024 | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely. Issue resolved
7 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | POWERGRID | IMPHAL | MN-05 | 132 kV Imphal (PG) end of Imphal ckt I | NP-8378-A | High time drift of 11 mins | 2024-09-09 | Till 10:30 Hrs of 30-10-2024 | IMPHAL | Other end meter used for drawal computation; time drift corrective action required. Issue resolved
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DULLAVCHERA FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | NAGALAND | SANIS |  | 132 kV SANIS END OF DOYANG | NE-0103-A | Standby Meter | Weekly Drift correction required
7 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132KV DOYANG END OF MOKOKCHUNG | NP-9053-A | Main Meter | Weekly Drift correction required
29 | ASSAM | PAILAPOOL |  | PAILAPOOL END OF JIRIBAM FDR | NP-8498-A | Main Meter | Weekly Drift correction required
30 | OTPC | PALATANA |  | PALATANA END OF SM NAGAR FDR | NP-9561-A | Check Meter | Weekly Drift correction required
31 | POWERGRID | AIZAWL |  | AIZAWL END OF MELRIAT FDR | NP-8485-A | Standby Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | TRIPURA | UDAIPUR | Time drift report not received
5 | ARUNACHAL | TENGA | Time drift report not received
6 | NAGALAND | KOHIMA | Time drift report not received
7 | NAGALAND | SANIS | Time drift report not received
8 | NEEPCO | AGBPP | Time drift report not received
9 | NEEPCO | DHEP | Time drift report not received
10 | NTPC | BGTPP | Time drift report not received
11 | POWERGRID | SALAKATI | Time drift report not received
12 | POWERGRID | SILCHAR | Time drift report not received
13 | POWERGRID | ROING | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Received on 06-11-2024
4 | ASSAM | AZARA | Received on 06-11-2024
5 | POWERGRID | ZIRO | Received on 06-11-2024
6 | MEGHALAYA | LUMSHNONG | Received on 06-11-2024
7 | MANIPUR | RENGPANG | Received on 06-11-2024
8 | MANIPUR | TIPAIMUKH | Received on 06-11-2024
9 | POWERGRID | AIZAWL | Received on 06-11-2024

## 04 NOV 24-10 NOV 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 0) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DULLAVCHERA FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | MIRZA |  | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
7 | NAGALAND | SANIS |  | 132 kV SANIS END OF DOYANG | NE-0103-A | Standby Meter | Weekly Drift correction required
8 | MEGHALAYA | NANGALBIBRA |  | 132kV NANGALBIBRA END OF AGIA | NP-9945-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | KILLING |  | 400KV Killing end of Bongaigaon | NP-8370-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Main Meter | Weekly Drift correction required
13 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
14 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BALIPARA |  | 220/132KV ICT-1(LV) | NP-6891-A | Standby Meter | Weekly Drift correction required
19 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | LUNGMUAL | Time drift report not received
2 | MIZORAM | KOLASIB | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | MEGHALAYA | UMTRU | Time drift report not received
5 | TRIPURA | UDAIPUR | Time drift report not received
6 | ARUNACHAL | TENGA | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGRID | SALAKATI | Time drift report not received
10 | POWERGRID | SILCHAR | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Received on 13-11-2024
3 | POWERGRID | KOLASIB | Received on 13-11-2024

## 11 NOV 24-17 NOV 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | IMPHAL | ZZ-40 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-I | NP-9635-A | Reads 0 | 18:15 Hrs of 21-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
8 | POWERGRID | IMPHAL | ZZ-43 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-II | NP-9545-A | Reads 0 | 19:15 Hrs of 13-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DULLAVCHERA FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | MIRZA |  | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
6 | ASSAM | KAHILIPARA |  | MeSEB –I (132kV Kahilipara-Umtru) feeder | NE-0088-A | Main Meter | Weekly Drift correction required
7 | NAGALAND | SANIS |  | 132 kV SANIS END OF DOYANG | NE-0103-A | Standby Meter | Weekly Drift correction required
9 | MEGHALAYA | KILLING |  | 400KV Killing end of Bongaigaon | NP-8370-A | Main Meter | Weekly Drift correction required
9 | MEGHALAYA | KILLING |  | 400KV Killing end of Silchar | NP-8371-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-I | NP-9544-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9706-A | Main Meter | Weekly Drift correction required
13 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9948-A | Standby Meter | Weekly Drift correction required
13 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
14 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | 132 kV LOKTAK END OF IMPHAL-I | NP-9508-A | Check Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV KOPILI #2 | NE-0062-A | Standby Meter | Weekly Drift correction required
19 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
19 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | MEGHALAYA | UMTRU | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | ARUNACHAL | TENGA | Time drift report not received
5 | NAGALAND | KOHIMA | Time drift report not received
6 | NAGALAND | SANIS | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | DHEP | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | OTPC | PALATANA | Time drift report not received
11 | POWERGRID | SILCHAR | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
3 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened (Software Issue Stated)
4 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened (Network Issue Stated)
5 | MANIPUR | NINGTHOUKONG | Not Received. Mailed to concerened (Network Issue Stated)
6 | MANIPUR | THOUBAL | Not Received. Mailed to concerened (Network Issue Stated)
7 | MANIPUR | RENGPANG | Not Received. Mailed to concerened (Network Issue Stated)
8 | POWERGRID | JIRIBAM | Received on 21-11-2024 (Network Issue Stated)
9 | MANIPUR | YUREMBAM | Received on 21-11-2024 (Network Issue Stated)
10 | MANIPUR | KARONG | Received on 20-11-2024 (Network Issue Stated)
11 | ASSAM | MIRZA | Received on 20-11-2024 (Network Issue Stated)

## 18 NOV 24-24 NOV 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-62 | 220/132 KV ICT-1(HV) | NP-6868-A | Erratic Reading (Around 66%). | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | IMPHAL | ZZ-40 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-I | NP-9635-A | Reads 0 | 18:15 Hrs of 21-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
8 | POWERGRID | IMPHAL | ZZ-43 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-II | NP-9545-A | Reads 0 | 19:15 Hrs of 13-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DULLAVCHERA FDR | NP-9904-A | Main Meter | Weekly Drift correction required
6 | ASSAM | MIRZA |  | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
6 | ASSAM | KAHILIPARA |  | MeSEB –I (132kV Kahilipara-Umtru) feeder | NE-0088-A | Main Meter | Weekly Drift correction required
7 | NAGALAND | SANIS |  | 132 kV SANIS END OF DOYANG | NE-0103-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9706-A | Main Meter | Weekly Drift correction required
13 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9948-A | Standby Meter | Weekly Drift correction required
13 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
14 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BNC |  | POLE II | NP-5798-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 3 | NE-0092-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV KOPILI #2 | NE-0062-A | Standby Meter | Weekly Drift correction required
19 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | ARUNACHAL | TENGA | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGID/STERLITE | NANGALBIBRA BAYS AT BONGAIGAON | Time drift report not received
10 | POWERGID | MISA | Time drift report not received
11 | POWERGID | ROING | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened
3 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened (Software Issue Stated)
4 | MANIPUR | NINGTHOUKONG | Not Received. Mailed to concerened (Network Issue Stated)
5 | MANIPUR | THOUBAL | Not Received. Mailed to concerened (Network Issue Stated)
6 | MANIPUR | RENGPANG | Received on 28-11-2024 (Network Issue Stated)
7 | POWERGRID | SILCHAR | Received on 27-11-2024

## 25 NOV 24-01 DEC 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for injection computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-58 | 220/132 KV ICT-2(LV) | NP-6890-A | Reads 0 | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | IMPHAL | ZZ-40 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-I | NP-9635-A | Reads 0 | 18:15 Hrs of 21-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
8 | POWERGRID | IMPHAL | ZZ-43 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-II | NP-9545-A | Reads 0 | 19:15 Hrs of 13-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
9 | POWERGRID | JIRIBAM (MA) | MN-19 | JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Erroneous reading | 16:00 Hrs of 01-12-2024 | Till end of the week | JIRIBAM | CT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | MIRZA |  | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
6 | ASSAM | KAHILIPARA |  | MeSEB –I (132kV Kahilipara-Umtru) feeder | NE-0088-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BNC |  | POLE II | NP-5798-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | BNC |  | 400 kV Lower Subansiri ckt 3 | NE-0092-A | Main Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV KOPILI #2 | NE-0062-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BADARPUR |  | 132kV Badarpur-Karimganj T/L | NP-7799-A | Standby Meter | Weekly Drift correction required
19 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
27 | NEEPCO | RANGANADI |  | Unit-1 | NP-5277-A | Standby Meter | Weekly Drift correction required
28 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
29 | NEEPCO | AgGBPS |  | Stn.Trans. # 2 | NP-9482-A | Standby Meter | Weekly Drift correction required
30 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
33 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Check Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | LINE # 3 (New Meter) | NP-9515-A | Check Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | ARUNACHAL | TENGA | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NEEPCO | AGBPP | Time drift report not received
6 | NEEPCO | DHEP | Time drift report not received
7 | NTPC | BGTPP | Time drift report not received
8 | POWERGID | ROING | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened
3 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
4 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
5 | MANIPUR | THOUBAL | Not Received. Mailed to concerened
6 | ARUNACHAL PRADESH | TENGA | Not Received. Mailed to concerened

## 02 DEC 24-08 DEC 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-58 | 220/132 KV ICT-2(LV) | NP-6890-A | Reads 0 | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | IMPHAL | ZZ-40 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-I | NP-9635-A | Reads 0 | 18:15 Hrs of 21-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
8 | POWERGRID | IMPHAL | ZZ-43 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-II | NP-9545-A | Reads 0 | 19:15 Hrs of 13-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
9 | POWERGRID | JIRIBAM (MA) | MN-19 | JIRIBAM(MAN) END OF JIRIBAM(PG)FDR | NP-9902-A | Erroneous reading | 16:00 Hrs of 01-12-2024 | 10:00 Hrs of 03-12-2024 | JIRIBAM | CT connectivity checking required. Phase disconnection likely
10 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
3 | ASSAM | TINSUKIA |  | KATHALGURI I | NP-9654-A | Standby Meter | Weekly Drift correction required
3 | ASSAM | TINSUKIA |  | KATHALGURI II | NP-9658-A | Standby Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | MIRZA |  | 400 KV MIRZA END OF SILCHAR FDR | NP-9981-A | Main Meter | Weekly Drift correction required
6 | ASSAM | KAHILIPARA |  | MeSEB –I (132kV Kahilipara-Umtru) feeder | NE-0088-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV Nangalbibra feeder | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400KV Misa#2 | NP-5285-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400KV B.Chariali#1 | NP-9485-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BNC |  | 132 Kv BNC- PAVOI Ckt-I (BNC end) | NP-9678-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BNC |  | POLE I | NP-7601-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | HAFLONG |  | Bay No.102 - Haflong - Umrangso | NP-8502-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | MARIANI_PG |  | MARIANI(PG) end of 220 kV MOKOKCHUNG-1 | NE-0046-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | MARIANI_PG |  | NEW MARIANI 400/220 kV ICT-I HV SIDE | NP-9951-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | Silchar #1 | NP 9928 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | SILCHAR |  | Misa 2 | NP-9896-A | Standby Meter | Weekly Drift correction required
17 | NBTL | NANGALBIBRA(ST) |  | 220 KV Nangalbibra-Bongaigaon CKT-1 ( Bay 213) | NE-0071-A | Standby Meter | Weekly Drift correction required
17 | NBTL | NANGALBIBRA(ST) |  | 220/132kV ICT-1 LV ( Bay-104) | NE-0099-A | Standby Meter | Weekly Drift correction required
17 | NBTL | NANGALBIBRA(ST) |  | 220/132kV ICT-2 LV ( Bay-105) | NE-0120-A | Standby Meter | Weekly Drift correction required
17 | NBTL | NANGALBIBRA(ST) |  | 132kV Nangalbibra MEPTCL-1 ( Bay-101) | NE-0156-A | Main Meter | Weekly Drift correction required
19 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
29 | NEEPCO | AgGBPS |  | Stn.Trans. # 2 | NP-9482-A | Standby Meter | Weekly Drift correction required
30 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
31 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
33 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Check Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Main Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | LINE # 3 (New Meter) | NP-9515-A | Check Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
1 | MANIPUR | YUREMBAM | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | MEGHALAYA | LUMSHNONG | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NTPC | BGTPP | Time drift report not received
8 | POWERGID | ROING | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | MANIPUR | THOUBAL | Not Received. Mailed to concerened
5 | ASSAM | SARUSAJAI | Mail Received on 12-12-2024. (Cable Issue)

## 09 DEC 24-15 DEC 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-58 | 220/132 KV ICT-2(LV) | NP-6890-A | Reads 0 | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | IMPHAL | ZZ-40 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-I | NP-9635-A | Reads 0 | 18:15 Hrs of 21-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
8 | POWERGRID | IMPHAL | ZZ-43 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-II | NP-9545-A | Reads 0 | 19:15 Hrs of 13-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
9 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF KHANDONG FDR | NE-0110-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
5 | ASSAM | KAHILIPARA |  | MeSEB –I (132kV Kahilipara-Umtru) feeder | NE-0088-A | Main Meter | Weekly Drift correction required
6 | ASSAM | AGIA |  | 132 kV Nangalbibra feeder | NP-9920-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
12 | NBTL | NANGALBIBRA(ST) |  | 220 KV Nangalbibra-Bongaigaon CKT-1 ( Bay 213) | NE-0071-A | Standby Meter | Weekly Drift correction required
13 | NBTL | NANGALBIBRA(ST) |  | 220/132kV ICT-2 LV ( Bay-105) | NE-0120-A | Standby Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
15 | NEEPCO | PANYOR |  | RANGANADI END OF 400KV BNC-2 | NP-9430-A | Check Meter | Weekly Drift correction required
16 | NEEPCO | PANYOR |  | RANGANADI END OF 400KV BNC-1 | NP-9429-A | Check Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BALIPARA |  | 400KV B.Chariali#1 | NP-9485-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BNC |  | 132 Kv BNC- PAVOI Ckt-I (BNC end) | NP-9678-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BNC |  | POLE I | NP-7601-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | HAFLONG |  | Bay No.102 - Haflong - Umrangso | NP-8502-A | Main Meter | Weekly Drift correction required
23 | POWERGRID | MISA |  | Silchar #1 | NP 9928 A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | SILCHAR |  | 400kV ICT 1 | NE-0050-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
30 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
31 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
32 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
33 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
34 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Check Meter | Weekly Drift correction required
38 | NEEPCO | AgGBPS |  | LINE # 3 (New Meter) | NP-9515-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | NAGALAND | KOHIMA | Time drift report not received
4 | NAGALAND | SANIS | Time drift report not received
5 | NEEPCO | AGBPP | Time drift report not received
6 | NEEPCO | DHEP | Time drift report not received
7 | NTPC | BGTPP | Time drift report not received
8 | POWERGID | ROING | Time drift report not received
9 | POWERGID | SALAKATI | Time drift report not received
10 | POWERGID | MISA | Time drift report not received
11 | POWERGID | HAFLONG | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
3 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
4 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened (Download Issue)
5 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened. (Cable Issue)
6 | POWERGRID | IMPHAL | Data for NP-9963-A, NE-0161-A, NP-8378-A not received. Mailed to concerned.

## 16 DEC 24-22 DEC 2024
1. Meter Reading Discripency
A. Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-58 | 220/132 KV ICT-2(LV) | NP-6890-A | Reads 0 | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | IMPHAL | ZZ-40 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-I | NP-9635-A | Reads 0 | 18:15 Hrs of 21-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
8 | POWERGRID | IMPHAL | ZZ-43 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-II | NP-9545-A | Reads 0 | 19:15 Hrs of 13-09-2024 | Till end of the week | IMPHAL | CT connectivity checking required. Phase disconnection likely
9 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
10 | MEGHALAYA | KHLEIHRIAT | ME-08 | 132KV KHLEIHRIAT(PG)-KHLEIHRIAT(ME) | NP-6866-A | Reads 0 | 01:15 Hrs of 21-12-2024 | Till end of the week | MEGHALAYA | CT/CVT connectivity checking required. Phase disconnection likely
B. Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | KAHILIPARA |  | MeSEB –I (132kV Kahilipara-Umtru) feeder | NE-0088-A | Main Meter | Weekly Drift correction required
5 | ASSAM | AGIA |  | 132 kV Nangalbibra feeder | NP-9920-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
11 | NBTL | NANGALBIBRA(ST) |  | 220 KV Nangalbibra-Bongaigaon CKT-1 ( Bay 213) | NE-0071-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | HAFLONG |  | Bay No.102 - Haflong - Umrangso | NP-8502-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | Silchar #1 | NP 9928 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
19 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | MEGHALAYA | LUMSHNONG | Time drift report not received
4 | MANIPUR | TIPAIMUKH | Time drift report not received
5 | NAGALAND | KOHIMA | Time drift report not received
6 | NAGALAND | SANIS | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | DHEP | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | POWERGID | MISA | Time drift report not received
4. Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | NAGALAND | SANIS | Not Received. Mailed to concerened

## 23 DEC 24-29 DEC 2024
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-58 | 220/132 KV ICT-2(LV) | NP-6890-A | Reads 0 | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID | IMPHAL | ZZ-40 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-I | NP-9635-A | Reads 0 | 18:15 Hrs of 21-09-2024 | 09:45 Hrs of 20-12-2024 | IMPHAL | -
8 | POWERGRID | IMPHAL | ZZ-43 | 400/132 KV 315 MVA IMPHAL L.V SIDE ICT-II | NP-9545-A | Reads 0 | 19:15 Hrs of 13-09-2024 | 10:00 Hrs of 20-12-2024 | IMPHAL | -
9 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
10 | MEGHALAYA | KHLEIHRIAT | ME-08 | 132KV KHLEIHRIAT(PG)-KHLEIHRIAT(ME) | NP-6866-A | Reads 0 | 01:15 Hrs of 21-12-2024 | 00:00 Hrs of 23-12-2024 | MEGHALAYA | -
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
2 | ASSAM | SONABIL |  | 220kV Sonabil-Balipara-II | NE-0035-A | Main Meter | Weekly Drift correction required
3 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
4 | ASSAM | KAHILIPARA |  | MeSEB –I (132kV Kahilipara-Umtru) feeder | NE-0088-A | Main Meter | Weekly Drift correction required
5 | ASSAM | AGIA |  | 132 kV Nangalbibra feeder | NP-9920-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
11 | NBTL | NANGALBIBRA(ST) |  | 220 KV Nangalbibra-Bongaigaon CKT-1 ( Bay 213) | NE-0071-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
12 | NEEPCO | PANYOR |  | BDTL-I | NP-9429A | Check Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BALIPARA |  | 400KV B.Chariali#3 | NP-9486-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BNC |  | 400 Kv Bus II SECTIONALIZER | NP-9084-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BNC |  | 401 kV Lower Subansiri ckt 2 | NE-0150-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | HAFLONG |  | Bay No.102 - Haflong - Umrangso | NP-8502-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | MISA |  | Silchar #1 | NP 9928 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
18 | STERLITE | AMPATI |  | 132 kV Ampati - Hatsingimari CKT-2 (Bay-107) | NE-0096-A | Standby Meter | Weekly Drift correction required
18 | STERLITE | HATSINGIMARI |  | 132kV Hastingimari- Ampati CKT-1 (Bay-109) | NE-0074-A | Standby Meter | Weekly Drift correction required
18 | STERLITE | HATSINGIMARI |  | 132kV Hastingimari- Ampati CKT-2 (Bay-110) | NE-0157-A | Standby Meter | Weekly Drift correction required
19 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Standby Meter | Weekly Drift correction required
20 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
21 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
22 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Main Meter | Weekly Drift correction required
23 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Mail | Weekly Drift correction required
19 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
20 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
21 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | NAGALAND | KOHIMA | Time drift report not received
5 | NAGALAND | SANIS | Time drift report not received
6 | NEEPCO | AGBPP | Time drift report not received
7 | NEEPCO | DHEP | Time drift report not received
8 | NTPC | BGTPP | Time drift report not received
9 | POWERGID | NIRJULI | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | ASSAM | SARUSAJAI | Mail Received on 01-01-2025. (Cable Issue)

## 30 DEC 24-05 JAN 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-58 | 220/132 KV ICT-2(LV) | NP-6890-A | Reads 0 | 00:00 Hrs of 05-06-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
8 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL - IMPHAL(PG) | NP-9603-A | Erroneous reading (reads around 5% less then earlier) | 05:30 Hrs of 30-12-2024 | Till end of the week | THOUBAL | CT/CVT connectivity checking required. Loose connection likely.
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
11 | NBTL | NANGALBIBRA(ST) |  | 220 KV Nangalbibra-Bongaigaon CKT-1 ( Bay 213) | NE-0071-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BNC |  | 400 Kv BNC- BLP Ckt-IV | NP-9059-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BNC |  | 33 Kv MVS I | NP-9676-A | Main Meter | Weekly Drift correction required
19 | POWERGRID | BNC |  | 400 Kv Bus II SECTIONALIZER | NP-9084-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | IMPHAL | NP-9598-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | HAFLONG |  | Bay No.102 - Haflong - Umrangso | NP-8502-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | MISA |  | DIMAPUR #1 | NE 0006 A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MISA |  | DIMAPUR #2 | NE 0023 A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MISA |  | Silchar #2 | NP 9929 A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 220 kV KOPILI #1 | NE 0061 A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MISA |  | 220 kV KOPILI #2 | NE 0062 A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MISA |  | ICT# 3 400 KV SIDE | NP 9401 A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | SALAKATI |  | 220 kV Salakati-Alipurduar line Ckt#1 | NP-7581-A | Main Meter | Weekly Drift correction required
29 | STERLITE | AMPATI |  | 132kV Hastingimari- Ampati CKT-1 (Bay-109) | NE-0074-A | Main Meter | Weekly Drift correction required
30 | STERLITE | AMPATI |  | 132kV Hastingimari- Ampati CKT-2 (Bay-110) | NE-0157-A | Main Meter | Weekly Drift correction required
31 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
32 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
33 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | LINE # 1 (New Meter) | NP-9513-A | Check Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Check Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
38 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
39 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
40 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
41 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
42 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
43 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
44 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
45 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | MANIPUR | TIPAIMUKH | Time drift report not received
4 | MEGHALAYA | UMTRU | Time drift report not received
5 | NEEPCO | AGBPP | Time drift report not received
5 | NEEPCO | PANYOR | Time drift report not received
6 | NTPC | BGTPP | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened (Software Issue)
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened (Cable Issue)
6 | MANIPUR | RENGPANG | Mail Received on 07-01-2025.

## 06 JAN 25-12 JAN 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | AS-58 | 220/132 KV ICT-2(LV) | NP-6890-A | Reads 0 | 00:00 Hrs of 05-06-2024 | 18:45 Hrs of 10-01-2025 | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
7 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
8 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL - IMPHAL(PG) | NP-9603-A | Erroneous reading (reads around 5% less then earlier) | 05:30 Hrs of 30-12-2024 | Till end of the week | THOUBAL | CT/CVT connectivity checking required. Loose connection likely.
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
3 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR | NP-9904 A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
11 | NBTL | NANGALBIBRA(ST) |  | 220 KV Nangalbibra-Bongaigaon CKT-2 ( Bay 212) | NE-0072-A | Standby Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508-A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
14 | INDIGRID | PKBARI |  | Tertiary | NP-9909-A | Check Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BNC |  | 132kV Itanagar ckt 1 | NP-9961-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | HAFLONG |  | Bay No.102 - Haflong - Umrangso | NP-8502-A | Main Meter | Weekly Drift correction required
22 | POWERGRID | MISA |  | DIMAPUR #1 | NE 0006 A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | MISA |  | DIMAPUR #2 | NE 0023 A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | MISA |  | Silchar #2 | NP 9929 A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MISA |  | 220 kV KOPILI #1 | NE 0061 A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | MISA |  | 220 kV KOPILI #2 | NE 0062 A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | MISA |  | ICT# 3 400 KV SIDE | NP 9401 A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | SALAKATI |  | 220 kV Salakati-Alipurduar line Ckt#1 | NP-7581-A | Main Meter | Weekly Drift correction required
29 | STERLITE | AMPATI |  | 132kV Hastingimari- Ampati CKT-1 (Bay-109) | NE-0074-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
39 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
40 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
41 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
42 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
43 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
44 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
45 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | TRIPURA | DHARMANAGAR | Time drift report not received
4 | MIZORAM | LUANGMUAL | Time drift report not received
5 | MANIPUR | TIPAIMUKH | Time drift report not received
6 | MEGHALAYA | LUMSHNONG | Time drift report not received
7 | NAGALAND | KOHIMA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
8 | POWERGRID | MISA | Time drift report not received
8 | POWERGRID | HAFLONG | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NTPC | BGTPP | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened (Software Issue)
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
6 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened (Cable Issue)
7 | POWERGRID | KHLEIRIAT | Mail Received on 15-01-2025.
8 | POWERGRID | MARIANI | Mail Received on 15-01-2025.
9 | POWERGRID | BALIPARA | Mail Received on 15-01-2025.
10 | POWERGRID | MISA | Mail Received on 15-01-2025.

## 13 JAN 25-19 JAN 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
7 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL - IMPHAL(PG) | NP-9603-A | Erroneous reading (reads around 5% less then earlier) | 05:30 Hrs of 30-12-2024 | Till end of the week | THOUBAL | CT/CVT connectivity checking required. Loose connection likely.
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | AGIA |  | 132 kV NANGALBIBRA END OF AGIA FDR | N9-9920-A | Main Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
3 | ASSAM | TINSUKIA |  | 220 kV Tinsukia end of AGBPP | NP-9658-A | Standby Meter | Weekly Drift correction required
3 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR | NP-9904 A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
11 | NBTL | NANGALBIBRA(ST) |  | 220 KV Nangalbibra-Bongaigaon CKT-1 ( Bay 213) | NE-0071-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BALIPARA |  | 400KV B.Chariali#2 | NP-9483-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | HAFLONG |  | Bay No.102 - Haflong - Umrangso | NP-8502-A | Main Meter | Weekly Drift correction required
27 | POWERGRID | MISA |  | New Mariani #2 | NP 9894 A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | SILCHAR |  | 400 kV Imphal 1 end at Silchar | NE-0007-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | SILCHAR |  | 400 kV Byrnihat end at Silchar | NP-9398-A | Standby Meter | Weekly Drift correction required
27 | POWERGRID | SILCHAR |  | 132kV ICT 3 | NE-0168-A | Standby Meter | Weekly Drift correction required
28 | POWERGRID | SALAKATI |  | 220 kV Salakati-Alipurduar line Ckt#1 | NP-7581-A | Main Meter | Weekly Drift correction required
38 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
39 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
40 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
41 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
42 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
43 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
44 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
45 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | TRIPURA | DHARMANAGAR | Time drift report not received
4 | MIZORAM | LUANGMUAL | Time drift report not received
5 | MANIPUR | TIPAIMUKH | Time drift report not received
6 | MEGHALAYA | LUMSHNONG | Time drift report not received
7 | NAGALAND | KOHIMA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NTPC | BGTPP | Time drift report not received
12 | POWERGRID | SALAKATI | Time drift report not received
13 | ASSAM | SARUSAJAI | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened (Software Issue)
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
6 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened (Cable Issue)
7 | ASSAM | KAHILIPARA | Not Received. Mailed to concerened
8 | NAGALAND | SANIS | Mail Received on 23-01-2025.
9 | MANIPUR | RENGPANG | Mail Received on 23-01-2025.
10 | ASSAM | BTPS | Mail Received on 22-01-2025.
11 | POWERGRID | KUMARGHAT | Mail Received on 22-01-2025.
12 | POWERGRID | SALAKATI | Mail Received on 22-01-2025.

## 20 JAN 25-26 JAN 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
7 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL - IMPHAL(PG) | NP-9603-A | Erroneous reading (reads around 5% less then earlier) | 05:30 Hrs of 30-12-2024 | Till end of the week | THOUBAL | CT/CVT connectivity checking required. Loose connection likely.
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
4 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR | NP-9904 A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
12 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
13 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | MISA |  | New Mariani #2 | NP 9894 A | Standby Meter | Weekly Drift correction required
15 | STERLITE | PK BARI |  | Bay 102_BJ NAGAR (TSECL LINE) | NP-9893-A | Main Meter | Weekly Drift correction required
16 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
17 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
18 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
19 | OTPC | PALATANA |  | 400kV LINE 2 CHECK | NE-0010-A | Check Meter | Weekly Drift correction required
20 | OTPC | PALATANA |  | GTG2 | NP-9471-A | Standby Meter | Weekly Drift correction required
21 | OTPC | PALATANA |  | 132kV LINE 2 CHECK | NP-8381-A | Check Meter | Weekly Drift correction required
22 | OTPC | PALATANA |  | 400kV SM Nagar Line 1 Main | NP-9944-A | Main Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
30 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
31 | NEEPCO | AgGBPS |  | STG # 1 | NP-9079-A | Check Meter | Weekly Drift correction required
32 | NEEPCO | AgGBPS |  | GTG # 4 | NP-9517-A | Check Meter | Weekly Drift correction required
33 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 3 (New Meter) | NP-9515-A | Main Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1) | NP-9940-A | Check Meter | Weekly Drift correction required
38 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Main Meter | Weekly Drift correction required
40 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
41 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2) | NP-9941-A | Main Meter | Weekly Drift correction required
42 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | TRIPURA | DHARMANAGAR | Time drift report not received
4 | MIZORAM | LUANGMUAL | Time drift report not received
5 | MANIPUR | TIPAIMUKH | Time drift report not received
6 | MEGHALAYA | LUMSHNONG | Time drift report not received
7 | NAGALAND | KOHIMA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NTPC | BGTPP | Time drift report not received
12 | POWERGRID | SALAKATI | Time drift report not received
13 | ASSAM | SARUSAJAI | Time drift report not received
14 | ARUNACHAL PRADESH | TENGA | Time drift report not received
15 | POWERGRID | MISA | Time drift report not received
16 | POWERGRID | ROING | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
6 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened
7 | ASSAM | KAHILIPARA | Mail Received on 29-01-2025
9 | MANIPUR | RENGPANG | Not Received. Mailed to concerened

## 27 JAN 25-02 FEB 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
7 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL - IMPHAL(PG) | NP-9603-A | Erroneous reading (reads around 5% less then earlier) | 05:30 Hrs of 30-12-2024 | Till end of the week | THOUBAL | CT/CVT connectivity checking required. Loose connection likely.
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | MEGHALAYA | LUMSHNONG |  | 132KV LUMSHNONG END OF PANCHGRAM FDR | NP-8384-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR | NP-9904 A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
7 | NBTL | NANGALBIBRA |  | 221 KV Nangalbibra-Bongaigaon CKT-2 ( Bay 212) | NE-0072-A | Standby Meter | Weekly Drift correction required
8 | NBTL | NANGALBIBRA |  | 220/132kV ICT-2 LV ( Bay-105) | NE-0120-A | Standby Meter | Weekly Drift correction required
9 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
13 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
14 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | New Mariani #2 | NP 9894 A | Standby Meter | Weekly Drift correction required
18 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
19 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
20 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
21 | OTPC | PALATANA |  | 400kV LINE 2 CHECK | NE-0010-A | Check Meter | Weekly Drift correction required
22 | OTPC | PALATANA |  | GTG2 | NP-9471-A | Standby Meter | Weekly Drift correction required
23 | OTPC | PALATANA |  | 132kV LINE 2 CHECK | NP-8381-A | Check Meter | Weekly Drift correction required
24 | OTPC | PALATANA |  | 400kV SM Nagar Line 1 Main | NP-9944-A | Main Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
30 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
31 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
32 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
33 | NEEPCO | AgGBPS |  | STG # 1 | NP-9079-A | Check Meter | Weekly Drift correction required
34 | NEEPCO | AgGBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
35 | NEEPCO | AgGBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
36 | NEEPCO | AgGBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
37 | NEEPCO | AgGBPS |  | LINE # 3 (Old Meter) | NP-9080-A | Check Meter | Weekly Drift correction required
38 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1) | NP-9940-A | Check Meter | Weekly Drift correction required
39 | NEEPCO | AgGBPS |  | LINE # 2 (Old Meter) | NP-9093-A | Check Meter | Weekly Drift correction required
40 | NEEPCO | AgGBPS |  | LINE # 2 (New Meter) | NP-9514-A | Main Meter | Weekly Drift correction required
41 | NEEPCO | AgGBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
42 | NEEPCO | AgGBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | TRIPURA | DHARMANAGAR | Time drift report not received
4 | MIZORAM | LUANGMUAL | Time drift report not received
5 | MANIPUR | TIPAIMUKH | Time drift report not received
6 | TRIPURA | AMBASSA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NTPC | BGTPP | Time drift report not received
14 | ARUNACHAL PRADESH | TENGA | Time drift report not received
15 | POWERGRID | MISA | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
6 | ASSAM | TINSUKIA | Mail Received on 05-02-2025
7 | ASSAM | SARUSAJAI | Mail Received on 05-02-2025
8 | MANIPUR | NINGTHOUKHONG | Mail Received on 06-02-2025

## 03 FEB 25-09 FEB 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | Till end of the week | BALIPARA | CT/CVT connectivity checking required. Phase disconnection likely
6 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
7 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL - IMPHAL(PG) | NP-9603-A | Erroneous reading (reads around 5% less then earlier) | 05:30 Hrs of 30-12-2024 | Till end of the week | THOUBAL | CT/CVT connectivity checking required. Loose connection likely.
8 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Reads zero | 00:00 Hrs of 03-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting to be checked
9 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads zero | 00:00 Hrs of 03-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | POWERGRID | DIMAPUR |  | KOHIMA FDR | NP-8472-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
4 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
5 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR | NP-9904 A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
7 | STERLITE | PK BARI |  | Bay 103- ICT-1 | NP-9906-A | Standby Meter | Weekly Drift correction required
8 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
12 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
13 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
14 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
15 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
16 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
17 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
18 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
19 | OTPC | PALATANA |  | 400kV LINE 2 CHECK | NE-0010-A | Check Meter | Weekly Drift correction required
20 | OTPC | PALATANA |  | GTG2 | NP-9471-A | Standby Meter | Weekly Drift correction required
21 | OTPC | PALATANA |  | 132kV LINE 2 CHECK | NP-8381-A | Check Meter | Weekly Drift correction required
22 | OTPC | PALATANA |  | 400kV SM Nagar Line 1 Main | NP-9944-A | Main Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
30 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | TRIPURA | DHARMANAGAR | Time drift report not received
4 | MIZORAM | LUANGMUAL | Time drift report not received
5 | MANIPUR | TIPAIMUKH | Time drift report not received
6 | TRIPURA | AMBASSA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NTPC | BGTPP | Time drift report not received
14 | ARUNACHAL PRADESH | TENGA | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
6 | ARUNACHAL PRADESH | DEOMALI | Mail Received on 12-02-2025
7 | ASSAM | SARUSAJAI | Not Received. Mailed to concerened
8 | POWERGRID | JIRIBAM | Mail Received on 12-02-2025
9 | POWERGRID | BONGAIGAON | Mail Received on 12-02-2025

## 10 FEB 25-16 FEB 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID | BALIPARA | ZZ-07 | BALIPARA END OF MISA FDR-2 | NP-5285-A | Erroneous reading | 00:00 Hrs of 23-09-2024 | 17:30 Hrs of 12-02-2025 | BALIPARA | -
6 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
7 | MANIPUR | THOUBAL | MN-29 | 400 kV THOUBAL - IMPHAL(PG) II | NP-9603-A | Erroneous reading (reads around 5% less then earlier) | 05:30 Hrs of 30-12-2024 | 14:45 Hrs of 12-02-2025 | THOUBAL | CT/CVT connectivity checking required. Loose connection likely.
8 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Reads zero | 00:00 Hrs of 03-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting to be checked
9 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads zero | 00:00 Hrs of 03-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | POWERGRID | DIMAPUR |  | KOHIMA FDR | NP-8472-A | Main Meter | Weekly Drift correction required
3 | ASSAM | HAILAKANDI |  | 132KV Silchar-1 (PGCIL) | NP-5301A | Main Meter | Weekly Drift correction required
4 | ASSAM | NALKATA |  | 132KV North Lakhimpur -Pare Line | NE-0117-A | Main Meter | Weekly Drift correction required
5 | POWERGRID | NIRJULI |  | ICT-II HV | NP-9662 A | Standby Meter | Weekly Drift correction required
6 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
7 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
8 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
9 | ASSAM | DULLAVCHERRA |  | 132 kV DULLAVCHERRA END OF DHARMANAGAR | NP-9904 A | Main Meter | Weekly Drift correction required
10 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
11 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
13 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
14 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
15 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
16 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
19 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
20 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
21 | STERLITE | SM NAGAR |  | SM NAGAR OLD (REMOTE END) | NP-9942-A | Standby Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | NAGALAND | KOHIMA | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | TRIPURA | DHARMANAGAR | Time drift report not received
5 | MIZORAM | LUANGMUAL | Time drift report not received
6 | MANIPUR | TIPAIMUKH | Time drift report not received
7 | TRIPURA | AMBASSA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NTPC | BGTPP | Time drift report not received
12 | NEEPCO | PANYOR | Time drift report not received
13 | ARUNACHAL PRADESH | TENGA | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
3 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
4 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
5 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
9 | POWERGRID | RANGIA | Mail Received on 19-02-2025

## 17 FEB 25-23 FEB 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | Till end of the week | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
6 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Reads zero | 00:00 Hrs of 03-02-2025 | 13:45 Hrs of 21-02-2025 | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting to be checked
7 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Sign Reversal | 13:45 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT reversal to be checked
8 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads zero | 00:00 Hrs of 03-02-2025 | 14:15 Hrs of 21-02-2025 | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting to be checked
9 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads 33% | 14:15 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting or two phase reversal to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
4 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
6 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
11 | MEGHALAYA | KILLING |  | 400KV Silchar | NP-8371-A | Main Meter | Weekly Drift correction required
12 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
14 | STERLITE | NANGALBIBRA(ST) |  | 221 KV Nangalbibra-Bongaigaon CKT-2 ( Bay 212) | NE-0072-A | Standby Meter | Weekly Drift correction required
15 | INDIGRID | SM NAGAR |  | Bay 101_SM NAGAR (TSECL LINE) | NP-9890-A | Main Meter | Weekly Drift correction required
16 | INDIGRID | SM NAGAR |  | SM NAGAR OLD (REMOTE END) | NP-9942-A | Standby Meter | Weekly Drift correction required
17 | INDIGRID | PKBARI |  | Bay 103- ICT-1 | NP-9906-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | NIRJULI |  | ICT-II HV | NP-9662 A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | HAFLONG |  | BAY NO 102 HFG-UMR | NP-8502-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | DIMAPUR |  | KOHIMA | NP-8472-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | BNC |  | 132kV Itanagar ckt 2 | NP-9962-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | BALIPARA |  | 400KV BONG#2 | NE-0047-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) | NP-6151-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | AGgBPS |  | STG # 2 | NP-9082-A | Standby Meter | Weekly Drift correction required
28 | NEEPCO | AGgBPS |  | Stn.Trans. # 1 | NP-9480-A | Standby Meter | Weekly Drift correction required
29 | NEEPCO | AGgBPS |  | LINE # 1 (Old Meter) | NP-9081-A | Main Meter | Weekly Drift correction required
30 | NEEPCO | AGgBPS |  | LINE # 2 (New Meter) | NP-9514-A | Check Meter | Weekly Drift correction required
31 | NEEPCO | AGgBPS |  | LINE # 4 (132KV AGTCCPP PK BARI LINE #1 Front Panel) | NP-9457-A | Check Meter | Weekly Drift correction required
32 | NEEPCO | AGgBPS |  | LINE # 5 (132KV AGTCCPP PK BARI LINE #2 Front Panel) | NP-9456-A | Check Meter | Weekly Drift correction required
33 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
34 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
35 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
36 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
37 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
38 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
39 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
40 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | NAGALAND | KOHIMA | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | TRIPURA | DHARMANAGAR | Time drift report not received
5 | MIZORAM | LUANGMUAL | Time drift report not received
6 | MANIPUR | TIPAIMUKH | Time drift report not received
7 | TRIPURA | AMBASSA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | POWERGRID | MISA | Time drift report not received
10 | POWERGRID | ROING | Time drift report not received
11 | NEEPCO | AGBPP | Time drift report not received
12 | NEEPCO | DOYANG | Time drift report not received
13 | NTPC | BGTPP | Time drift report not received
14 | NEEPCO | PANYOR | Time drift report not received
15 | ARUNACHAL PRADESH | TENGA | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
4 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
5 | POWERGRID | RANGIA | Mail Received on 26-02-2025
6 | POWERGRID | LUANGMUAL | Mail Received on 26-02-2025 (Software issue)
7 | ASSAM | SONABIL | Mail Received on 27-02-2025 (Software issue)

## 24 FEB 25-02 MAR 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | POWERGRID/TRIPURA | SMNAGAR(TSECL) | TR-13 | 132 kV SM NAGAR (TSECL) - PALATANA | NP-8471-A | Erroneous reading (Close to zero) | 11:30 Hrs of 02-12-2024 | 18:30 Hrs of 01-03-2025 | POWERGRID/TRIPURA | Other end meter used for drawal computation. CT connectivity checking required. Phase disconnection likely
6 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Sign Reversal | 13:45 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT reversal to be checked
7 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads 33% | 14:15 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting or two phase reversal to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
4 | POWERGRID | ROING |  | Chapakhawa-1 | NE-0059-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR I | NP-9680-A | Main Meter | Weekly Drift correction required
6 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
7 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
8 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
11 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
12 | MEGHALAYA | KILLING |  | 400KV Silchar | NP-8371-A | Main Meter | Weekly Drift correction required
13 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Main Meter | Weekly Drift correction required
15 | POWERGRID | NIRJULI |  | ICT-II HV | NP-9662 A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | HAFLONG |  | BAY NO 102 HFG-UMR | NP-8502-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | KOHIMA | NP-8472-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BNC |  | 132kV Itanagar ckt 2 | NP-9962-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BALIPARA |  | 400KV BONG#2 | NE-0047-A | Standby Meter | Weekly Drift correction required
23 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) | NP-6151-A | Standby Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
30 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
31 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | NAGALAND | KOHIMA | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | TRIPURA | DHARMANAGAR | Time drift report not received
5 | MIZORAM | LUANGMUAL | Time drift report not received
6 | MANIPUR | TIPAIMUKH | Time drift report not received
7 | TRIPURA | AMBASSA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NTPC | BGTPP | Time drift report not received
12 | POWERGRID | BALIPARA | Time drift report not received
13 | ARUNACHAL PRADESH | TENGA | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
4 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
5 | MIZORAM | KOLASIB | Mail Received on 05-03-2025
6 | MIZORAM | LUANGMUAL | Not Received. Mailed to concerened
7 | MANIPUR | KARONG | Mail Received on 05-03-2025
8 | POWERGRID | SALAKATI | Mail Received on 05-03-2025
9 | ASSAM | SARUSAJAI | Mail Received on 06-03-2025

## 03 MAR 25-09 MAR 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
6 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Sign Reversal | 13:45 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT reversal to be checked
7 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads 33% | 14:15 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting or two phase reversal to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
4 | ASSAM | MIRZA |  | Bongaigaon 400 kV | NP-9983-A | Main Meter | Weekly Drift correction required
5 | ASSAM | AGIA |  | 132 kV AGIA END OF NANGALBIBRA | NP-9920-A | Main Meter | Weekly Drift correction required
6 | POWERGRID/ASSAM | CHAPAKHOWA |  | Roing-1 | NE-0059-A | Main Meter | Weekly Drift correction required
7 | POWERGRID/ASSAM | CHAPAKHOWA |  | Roing-2 | NE-0056-A | Main Meter | Weekly Drift correction required
8 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
12 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
13 | MANIPUR | THOUBAL |  | 400 kV THOUBAL END OF IMPHAL II | NP-9603-A | Standby Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
15 | STERLITE | NANGALBIBRA |  | 220 KV Nangalbibra-Bongaigaon CKT-2 ( Bay 212) | NE-0072-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | NIRJULI |  | ICT-II HV | NP-9662 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | HAFLONG |  | BAY NO 102 HFG-UMR | NP-8502-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | KOHIMA | NP-8472-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BNC |  | POLE II | NP-5798-A | Main Meter | Weekly Drift correction required
23 | POWERGRID | BALIPARA |  | 400KV BONG#2 | NE-0047-A | Standby Meter | Weekly Drift correction required
24 | POWERGRID | BALIPARA |  | 220/132KV ICT-2(HV) | NP-6151-A | Standby Meter | Weekly Drift correction required
25 | POWERGRID | MARIANI |  | 400/220 NEW MARIANI ICT-II HV SIDE | NP-9950-A | Standby Meter | Weekly Drift correction required
26 | POWERGRID/MIZORAM | SIHHMUI |  | SHIMUI END OF MELRIAT II FDR | NP-9493-A | Main Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
30 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
31 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
32 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
33 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
34 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | NAGALAND | KOHIMA | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | TRIPURA | DHARMANAGAR | Time drift report not received
5 | MIZORAM | LUANGMUAL | Time drift report not received
6 | MANIPUR | TIPAIMUKH | Time drift report not received
7 | TRIPURA | AMBASSA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NEEPCO | PANYOR | Time drift report not received
12 | NTPC | BGTPP | Time drift report not received
13 | POWERGRID | BALIPARA | Time drift report not received
14 | ARUNACHAL PRADESH | TENGA | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
4 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
5 | MIZORAM | LUANGMUAL | Mail Received on 13-03-2025 (Software Issue)
6 | POWERGRID | RANGIA | Mail Received on 12-03-2025
7 | ASSAM | KAHELIPARA | Mail Received on 12-03-2025

## 10 MAR 25-16 MAR 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | Till end of the week | IMPHAL | Other end meter used for drawal computation; CT/PT connectivity checking required
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Sign Reversal | 13:45 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT reversal to be checked
6 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads 33% | 14:15 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting or two phase reversal to be checked
7 | MEGHALAYA | KHLIEHRIAT | ME-02 | 132 kV KHLRT(MeSEB) END OF KHLRT(PG) FDR-1 | NP-6865-A | Erroneous reading. Reads close to zero | 12:15 Hrs of 10-03-2025 | Till end of the week | KHLIEHRIAT | CT/CVT connectivity checking required. CT shorting/VT open to be checked
8 | NEEPCO | KHANDONG | KK-01 | 132 KV KHANDONG END OF UMRANGSHU | NE-0136-A | Erroneous reading. Reads 33% | 23:00 Hrs of 13-03-2025 | Till end of the week | KHANDONG | Other end meter used for injection computation. CT/CVT connectivity checking required. CT shorting/VT Open or two phase reversal to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | NEEPCO | KHANDONG | KK-10 | 3 Mva X’er | NE-0174-A | High time drift | 2023-10-16 | Till end of the week | KHANDONG | Very High Time drift. Time drift corrective action required
3 | NEEPCO | KHANDONG | KK-18 | 3 Mva X’er | NE-0172-A | High time drift | 2023-10-16 | Till end of the week | KHANDONG | Very High Time drift. Time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
3 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
4 | ASSAM | MIRZA |  | Bongaigaon 400 kV | NP-9983-A | Main Meter | Weekly Drift correction required
6 | POWERGRID/ASSAM | CHAPAKHOWA |  | Roing-1 | NE-0059-A | Main Meter | Weekly Drift correction required
8 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
9 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
10 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-II | NP-9546-A | Main Meter | Weekly Drift correction required
11 | MANIPUR | YUREMBAM |  | 132kVYUREMBAM END OF IMPHAL-III | NP-9706-A | Standby Meter | Weekly Drift correction required
12 | MANIPUR | YUREMBAM |  | 132kV YUREMBAM END OF KARONG | NP-9948-A | Standby Meter | Weekly Drift correction required
14 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
16 | POWERGRID | NIRJULI |  | ICT-II HV | NP-9662 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | MISA |  | ICT#2 220 KV SIDE | NE 0008 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | HAFLONG |  | BAY NO 102 HFG-UMR | NP-8502-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | DIMAPUR |  | KOHIMA | NP-8472-A | Standby Meter | Weekly Drift correction required
22 | POWERGRID | BNC |  | POLE II | NP-5798-A | Main Meter | Weekly Drift correction required
23 | POWERGRID | BALIPARA |  | 400KV B.Chariali#2 | NP-9483-A | Standby Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
30 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
31 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
32 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
33 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
34 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | NAGALAND | KOHIMA | Time drift report not received
3 | TRIPURA | UDAIPUR | Time drift report not received
4 | TRIPURA | DHARMANAGAR | Time drift report not received
5 | MIZORAM | LUANGMUAL | Time drift report not received
6 | MANIPUR | TIPAIMUKH | Time drift report not received
7 | TRIPURA | AMBASSA | Time drift report not received
8 | NAGALAND | SANIS | Time drift report not received
9 | NEEPCO | AGBPP | Time drift report not received
10 | NEEPCO | DOYANG | Time drift report not received
11 | NEEPCO | PANYOR | Time drift report not received
12 | NTPC | BGTPP | Time drift report not received
14 | ARUNACHAL PRADESH | TENGA | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
4 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
4 | NEEPCO | KHANDONG | Seure Meter data Not Received. Mailed to concerened
5 | MANIPUR | YUREMBAM | Mail Received on 19-03-2025
6 | MIZORAM | KOLASIB | Mail Received on 19-03-2025
7 | ASSAM | SARUSAJAI | Mail Received on 19-03-2025